YTD-G SERIES INVERTER

USER MANUAL

SHANGHAI YATAI INSTRUMENT CO.,LTD

CONTENTS

I  Operation in Safety ……………………………………………….……1

II  Products ………………………………...…………………………..…....3

2.1 Models & Nameplate ………………...………………………………..3

2.2 Products List……………………………………… …………………..3

2.3 Appearance ....………………………………………………………….5

2.4 Performance Indexes …………………………………………………..6

III  Installation & Wiring ……………...…………………............................7

3.1 Installation …….……………………………………………………….7

3.2 Wiring …...…………………………………………………………….9

IV  Operation & Display ………..………………………………………....16

4.1 Keypad Control Unit ……………………………………………...….16

4.2 Function Parameters Setting…………………………..…………..….18

4.3 Function Code Grouping……………..……………………………….19

4.4 Panel Display.………….………………………………………….….19

V  Functions & Parameters Instruction …………………...………….…....20

5.1 Basic Parameters…….……………….………………………….……20

5.2 Operation Control Parameters …………………………………..........24

5.3 Multi-Speed Parameters ……..……………………….……..………..30

5.4 Programmable Input & Output Terminal Parameters...…………........33

5.5 V/F Control Parameters ……..…………………………..………....…36

5.6 PI Setting Parameters …………………………..………………….....39

5.7 Timing Control & Definable Protection Parameters ………….…..….41

5.8 Analog signal Parameters…………………………….…………...…..43

5.9 Communication Parameters …………..…………….……………......44

VI  Simple Mode of Operation ………………………..…………………...46

6.1 Operation Mode Block Diagram …………………………..……..…..46

6.2 Speed Control Mode …….………………………………….………..46

Appendix 1 Trouble Shooting…………………….……………….….…..…55

Appendix 2 Function-Codes Zoom Table……………...……………………58

Appendix 3 Selection of Braking Resistor and Braking unit …...…………..67

I. Operation in Safety

Hazard!

◆ Inverter is not allowed to install in a place with flammable or explosive gases in case explosion may be triggered off. ◆ Only competent professionals can handle installation, wiring, operation and maintenance on inverter. ◆ Inverter grouding terminal PE（ ）shall be well connected to earth (grounding impedance not more than 4Ω). ◆ Shortcircuit is not allowed between common point (CM) and reference point (GND or AGND) for inverter’s internal power supply and input zero line or inverter’s own “N” teminal. ◆ Make sure that wiring is properly connected and cover-board is well fixed prior to inverter switch-on; ◆ Do not touch inveter’s charged terminals with hands after it is switched on. ◆ Swich off before conducting any wiring or maintenance. ◆ No maintenance is allowed within the first 10 minutes after switch-off or when DC bus voltage exceeds 36V. Do not touch internal circuit or components.

Warning!

◆ Make sure for a proper input voltage with inverter before it is connected with power. ◆ Do not drop such metal objects as screwdriver or screw into inverter. ◆ Do not install inverter in a place with direct sunlight. Do not stem inverter’s vent. ◆ Do not connect input power to Teminals U, V, W or PE, P, B (N). ◆ No direct connection of braking resistor to Terminal P or N. ◆ Control loop wiring shall be separate from power loop wiring to avoid possible interference.

Warning!

♦ Please read this manual carefully before any operation on inverter.

♦ Inverter should not be stored or installed where there is strong vibration, strong erosion, heavy dust, high temperature or greater humidity.

♦ Regular check shall be required for a proper wiring with inverter’s input and output, and to make sure that the other wirings of the equipment are not aging.

♦ Check is required for motor insulation resistance before installation and operation.

♦ Extra cooling measures shall be necessary if motor often runs at low speed.

♦ Braking resistor or braking unit shall be adopted to avoid frequent over-voltage or over-current in case of negative-torque energy feedback.

♦ Neither variable resistor or capacitance should be connected to inverter’s output to improve power factor。Do not install a breaker between inverter’s output and motor. Should a breaker have to be installed, it shall be ensured that it works only when inverter output current reads zero.

♦ YTD-G inverter has a safety level of IP20.

♦ Cleaning is recommended on inverter’s internal components and radiator after it is in use for 1~3 months. Should it not be used for a long time, inverter should be switched on at a certain interval (better one month).

II. Products

2.1 Models & Nameplate

Product model is interpreted as below (taking for instance the three-phase 2.2KW inverter with internal braking unit).

YTD-G series inverter’s nameplate is illustrated as Fig 2-2 (taking the three-phase 2.2KW inverter for instance).

AC: alternating current input.

3PH:three-phase

380V and 50/60Hz : rated input voltage and frequency

2.2KW and 6.5A: inverter’s rated power and rated output current

0～380V:inverter’s output voltage range.

0.00～400.0Hz: output frequency range

2.2 Product List

YTD-G series inverter’s power range: 0.75～400KW. For main information, refer to Table 2-1.

For inverter’s external dimensions and installation dimensions, please refer to Table 3-2.

Table 2-1            YTD-G Product List

| Models | Rated Input Voltage（V） | Rated Output Current (A) | Structure Code | ApplicableMotor (KW) | Remarks |
| --- | --- | --- | --- | --- | --- |
| YTD0.75G2T1B | ～220(three -phase) | 4.5 | B0 | 0.75 | Three-phase inverter (with internal braking unit) |
| YTD1.5G2T1B | ～220(three -phase) | 8 | B1 | 1.5 |  |
| YTD2.2G2T1B | ～220 (three -phase) | 10 | B1 | 2.2 |  |
| YTD0.75G4T1B | ~380V(three-phase) | 2 | B0 | 0.75 |  |
| YTD1.5G4T1B | ～380 (three-phase) | 5 | B1 | 1.5 |  |
| YTD2.2G4T1B | ～380 (three-phase) | 6.5 | B1 | 2.2 |  |
| YTD3.7G4T1B | ～380 (three-phase) | 8 | B1 | 3.7 |  |
| YTD5.5G4T1C | ～380 (three-phase) | 12 | B2/C1 | 5.5 |  |
| YTD7.5G4T1C | ～380 (three-phase) | 17 | B2/C1 | 7.5 |  |

Table 2-1 continued

| Models | Rated Input Voltage（V） | Rated Output Current (A) | Structure Code | ApplicableMotor (KW) | Remarks |
| --- | --- | --- | --- | --- | --- |
| YTD11G4T1C | ～380 (three-phase) | 23 | C2 | 11 | three-phase inverter (without internal braking unit) |
| YTD15G4T1C | ～380 (three-phase) | 32 | C2 | 15 |  |
| YTD18.5G4T1C | ～380 (three-phase) | 38 | C3 | 18.5 |  |
| YTD22G4T1C | ～380 (three-phase) | 44 | C3 | 22 |  |
| YTD30G4T1C | ～380 (three-phase) | 60 | C4 | 30 |  |
| YTD37G4T1C | ～380 (three-phase) | 75 | C4 | 37 |  |
| YTD45G4T1C | ～380 (three-phase) | 90 | C4 | 45 |  |
| YTD55G4T1C | ～380 (three-phase) | 110 | C5 | 55 |  |
| YTD75G4T1C | ～380 (three-phase) | 150 | C5 | 75 |  |
| YTD90G4T1C | ～380 (three-phase) | 180 | C6 | 90 |  |
| YTD110G4T1C | ～380 (three-phase) | 220 | C6 | 110 |  |
| YTD132G4T1C | ～380 (three-phase) | 265 | C7 | 132 |  |
| YTD160G4T1C | ～380 (three-phase) | 320 | C7 | 160 |  |
| YTD30G4T1D | ～380 (three-phase) | 60 | D1 | 30 |  |
| YTD37G4T1D | ～380 (three-phase) | 75 | D2 | 37 |  |
| YTD45G4T1D | ～380 (three-phase) | 90 | D2 | 45 |  |
| YTD55G4T1D | ～380 (three-phase) | 110 | D3 | 55 |  |
| YTD75G4T1D | ～380 (three-phase) | 150 | D3 | 75 |  |

Table 2-1 continued

| Models | Rated Input Voltage（V） | Rated Output Current (A) | Structure Code | ApplicableMotor (KW) | Remarks |
| --- | --- | --- | --- | --- | --- |
| YTD90G4T1D | ～380 (three-phase) | 180 | D4 | 90 |  |
| YTD110G4T1D | ～380 (three-phase) | 220 | D4 | 110 |  |
| YTD132G4T1D | ～380 (three-phase) | 265 | D5 | 132 |  |
| YTD160G4T1D | ～380 (three-phase) | 320 | D5 | 160 |  |
| YTD185G4T1D | ～380 (three-phase) | 370 | D5 | 185 |  |
| YTD200G4T1D | ～380 (three-phase) | 400 | D5 | 220 |  |
| YTD220G4T1D | ～380 (three-phase) | 440 | D5 | 220 |  |
| YTD250G4T1D | ～380 (three-phase) | 490 | D5 | 250 |  |
| YTD280G4T1D | ～380 (three-phase) | 550 | D6 | 280 |  |
| YTD315G4T1D | ～380 (three-phase) | 620 | D6 | 315 |  |
| YTD400G4T1D | ～380 (three-phase) | 800 | D6 | 400 |  |

2.3 Performance Indexes

Table 2-2

| Items | Descriptions |
| --- | --- |
| Input | Rated Voltage | three-phase 380V±15%（ three-phase 220V±15%） |
|  | Rated Frequency | 50/60Hz（±5%） |
| Output | Rated Voltage | three-phase 0～380V;three-phase 0～220V |
|  | Frequency Range | 0.00～400.0Hz (frequency resolution ratio0.01Hz) |
|  | Overload Capacity | 150％ 60S |
| Control Mode | Frequency Setting Accuracy | Digit Setting: 0.01Hz, Analog signal Setting: Max Frequency×0.4％ |
|  | Setting Mode | optimized space vector control |
|  | V/F Curve | 3 kinds of V/F curves. To select and set beeline V/F curve, polygonal line V/F curve and square V/F curve as per load |

Table 2-2 continued

| Items | Descriptions |
| --- | --- |
|  | Torque Promotion | Manual setting torque promotion within 1～15％ |
|  | Automatic Voltage Setting | Automatic setting output voltage to meet input power fluctuation within certain range |
|  | Braking Mode | DC Braking＋Optimized Energy-consumption Braking |
|  | PI Adjusting | With built-in PI adjuster for automatic control |
|  | Jogging | Jogging Range: 0.00～400.0Hz |
|  | Automatic Circular Running | User will program output frequency mode as per process requirements |
| Operation Function | Frequency Setting | Digit frequency setting, keypad “▲/▼” keys setting, “UP” and “DOWN” terminals setting; Keypad potentiometer or external analog signal (0～5V, 0～20mA) setting; Analog channel compound operation setting; Multi-stage speed control and coding speed control; communication control box / computer setting. |
|  | Start/Stop Control | Control over keypad, communication control box, terminals and computer |
| Protection Function | Input out-phase, input undervoltage, over-voltage, over-current, inverter overload, motor overload, overheat, current check trouble, peripheral equipment trouble, user password error/exterior interference, contactor monitoring. |
| Display | LED nixie tube showing present output frequency, present rotate-speed, present output current, present output voltage, final axis linear-velocity, exterior pulse count-value, types of error, function-code parameters and operation parameters; 4 LED indicators showing the current working status of inverter. |
| Environment Conditions | Equipment Location | Free of tangy caustic gases or dust |
|  | Environment Temperature | -10℃～+50℃ |
|  | Environment Humidity | Below 90% (no water-bead coagulation) |
|  | Vibration Strength | Below 0.5g (acceleration) |
|  | height above sea level | Below 1000 meters |
| Applicable Motor Power | 0.75～400KW |

III. Installation & Wiring

3.1 Installation

3.1.1 Installation Direction & Space

For better heat radiation of inverter, it should be installed perpendicularly ( as shown in Fig 3-1) while ventilation space shall be secured in the surroundings. For clearance dimensions for installation of inverter,refer to Table 3-1 (recommended)

Table3-1        Clearance Dimensions

| Inverter Type | Clearance Dimensions |
| --- | --- |
| Hanging Type（＜22KW） | A≥150mm | B≥50mm |
| Hanging Type （≥22KW） | A≥200mm | B≥75mm |
| Cabinet Type（75～110KW） | C≥200mm | D≥75mm |

3.1.2 Installation Environment

◆ No drenching, dripping, steam, dust or oily dust; no caustic, flammable gases, liquid; no metal particles or metal powder.

◆ Environment temperature: within -10℃～+50℃.

◆ Environment relative humidity: below 90%, without water-bead coagulation.

◆ Vibration strength: below 0.5g (acceleration).

◆ Ventilation should be secured should inverter be installed inside a control cabinet.

3.1.3 External Dimensions & Installation Dimensions

Table 3-2    YTD-G Product Dimension List

| Structure Code | External Dimensions (A×B×H) | Installation Dimensions (W×L) | Mounting Screws | Remarks |
| --- | --- | --- | --- | --- |
| B0 | 120×135×200 | 108×1955 | M4 | Plastic Housing Hanging Type |
| B1 | 150×155×225 | 118×215 | M4 |  |
| B2 | 200×155×310 | 194×304 | M4 |  |
| C1 | 214×244×366 | 160×346 | M8 | Metal Hanging Type |
| C2 | 255×234×380 | 200×360 | M8 |  |
| C3 | 275×326×460 | 220×440 | M8 |  |
| C4 | 360×326×570 | 300×540 | M8 |  |
| C5 | 545×340×810 | 400×780 | M8 |  |
| C6 | 545×340×950 | 400×920 | M8 |  |
| C7 | 545×340×1080 | 440×1000 | M10 |  |
| D1 | 400×400×1170 | 350×300 | M10 | Metal Cabinet Type |
| D3 | 500×450×1400 | 300×220 | M12 |  |
| D4 | 600×500×1600 | 370×300 | M16 |  |
| D5 | 760×550×1980 | 500×320 | M16 |  |
| D6 | 800×600×1980 | 500×320 | M16 |  |

3.2 Wiring

3.2.1 Standard Wiring Diagram

● Control loop wiring shall be separate from main loop wiring, and should never be laid in the same wiring duct to avoid any possible interference.

● Control wiring should adopt shielded split-conductor, with section-area of 0.3～0.5mm2 for Lead,but signal wire should not be too long.

Wiring mode for inverter’s main loop and control loop are indicated as in the followings:

Fig 3-3 standard wiring diagram for single-phase inverter (including three-phase 220 VAC input inverter).

Fig 3-4 standard wiring diagram for three-phase inverter.

Note: Braking resistor and braking unit are both optional. Refer to Appendix 3 for standards of optionals.

Wiring Diagram 1

Wiring Diagram 2

Notes:

Note 1. Single-phase 220V inverter is only connected to L1 and L2.

Note 2. Terminals P and B in Wiring Diagram 2 are connected to braking resistor while Terminals P and N are connected to braking unit, Terminals P+ and P, to reactor, as per main loop terminals.

3.2.2 Input & Output Terminals

1）Power Terminals:

a)Three-Phase 220V ≤2.2KW

| PE | L1 | L2 | L3 | P | B | U | V | W |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

b)Three-Phase 2.2~15KW

| PE | R | S | T | P | B | U | V | W |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

c)Three-Phase 18.5~160KW

| PE | R | S | T | U | V | W | P+ | P | N |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

d)Three-Phase 30~400KW

| PE | R | S | T | P | N | U | V | W |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Table 3-3          Main Loop Terminals Description

| Terminals | Terminal Marking | Terminal Function Description |
| --- | --- | --- |
| Power Input Terminal | R, S, T | Three-phase 380V AC input terminals. |
| Output Terminal | U, V, W | Inverter power output terminal, connected to motor. |
| Grounding Terminal | PE | Inverter grounding terminal or connected to ground. |
| Braking Terminal | P, B | External braking resistor (Note: no Terminals P or B for inverter without built-in braking unit). |

Table 3-3 continued

| Braking Terminal | P, N | DC bus-line output, externally connected to braking resistor. P connected to input terminal “P” of braking unit or terminal “+”, N connected to input terminal of braking unit “N” or terminal “－”. |
| --- | --- | --- |
|  | P, P+ | Externally connected to reactor. |

Table 3-4      Wiring Recommended for Input/Output Loop

| Inverter Model | Lead Section Area (mm2) | Inverter Model | Lead Section Area (mm2) |
| --- | --- | --- | --- |
| YTD2.2G4T1B | 2.5 | YTD75G4T1C | 60 |
| YTD3.7G4T1B | 2.5 | YTD90G4T1C | 60 |
| YTD5.5G4T1C | 4.0 | YTD110G4T1C | 60 |
| YTD7.5G4T1C | 4.0 | YTD132G4T1C | 75 |
| YTD11G4T1C | 6 | YTD160G4T1C | 75 |
| YTD15G4T1C | 10 | YTD185G4T1C | 95 |
| YTD18.5G4T1C | 16 | YTD200G4T1C | 100 |
| YTD22G4T1C | 16 | YTD220G4T1C | 120 |
| YTD30G4T1C | 25 | YTD250G4T1C | 150 |
| YTD37G4T1C | 25 | YTD280G4T1C | 150 |
| YTD45G4T1C | 35 | YTD315G4T1C | 175 |
| YTD55G4T1C | 35 | YTD400G4T1C | 200 |

Warning: Power terminal shall be tightly secured!

2) Control Terminal:

a) ＜5.5KW

| OP1 | OP2 | OP3 | OP4 | OP5 | OP6 | OP7 | OP8 | CM | IM | FM | I2 | VCC | V2 | GND | TA | TB | TC | OUT | +24V |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

b) ≥5.5KW

| OP1 | OP2 | OP3 | OP4 | OP5 | OP6 | OP7 | OP8 | CM | IM | FM | V1 | V2 | GND | TA | TB | TC | OUT | +24V |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Warning: Fastening moment for control terminal: 5kgf.cm.

Table 3-5           Control Terminal Functions

| Classification | Terminal | Mfg Function | Function Description | Specification |
| --- | --- | --- | --- | --- |
| Output signal of Switching Value | OUT | Operation Indication Signal | Indicating inverter’s operation status. OUT:collector open-circuit output with output current not more than 100mA. | Refer to Function Code F416、F417 for other function settings. |
|  | TA | Fault Indication Signal | Indicating inverter’s fault status. TC: common point; TB-TC: normally closed contact ，TA-TC: normally open contact. Contact spec: 12A 125VAC 7A 250VAC 7A 30VDC |  |
|  | TB |  |  |  |
|  | TC |  |  |  |
| Analog Output Signal | FM | Voltage Output | Output voltage is proportional to output frequency (or current). | Output voltage range:0～10V Max output current 10mA |
|  | IM | Current Output | Output current is proportional to output frequency (or current). | Output current range: 0(4)～20mA. Terminal’s external load impedance not more than 500Ω. |
| Power Reference | VCC | Voltage Source | 5V power reference, power reference point: GND terminal. | DC：＋5V<100mA |
| Voltage & Current Analog signal Input Terminal | V2 | Voltage Input | Both terminals are used for analog signal speed control and PI setting & feedback. V2 input 0~5V or 0~10V, subject to jumper-terminal | Input voltage:0～5（10）V Input impedance:78KΩ |
|  | I2 | Current Input |  | Input current: 0（4）～20mA Input impedance:500Ω |
| Reference Gnd | GND | Reference Gnd | Reference gnd for VCC voltage source | Connected with “GND”, “PE” or “N” terminals is unallowed. |
| Power Source | 24V | Control Power Supply | Accessory power-supply for input terminal,Power-supply common port is CM terminal. | DC：＋24V <200mA |

Table 3-5 continued

| Classification | Terminal | Mfg Function | Function Description | Specification |
| --- | --- | --- | --- | --- |
| Common Port | CM | Common Port | Common port for OP1～OP8 terminal and 24V power-supply. | Connected with “GND”, “PE” or “N” terminal is unallowed. |
| External Control Terminal Input | OP1 | Jogging Corotation | Connection between this terminal and CM can affect jogging forward running. | Refer to F408～F415 for other function settings. |
|  | OP2 | Multi-stag Speed Control Terminal | “Multi-stage Speed” transfer terminal. |  |
|  | OP3 |  |  |  |
|  | OP4 |  |  |  |
|  | OP5 | External Emergency Stop | Input emergency stop signal, and inverter will display “ESP” fault signal. |  |
|  | OP6 | “FWD” Terminal | Refer to Table 5-2 (P29) Terminal Control Mode for inverter terminals running control terminal. |  |
|  | OP7 | “REV” Terminal |  |  |
|  | OP8 | Reset | Connection between this terminal and CM can reset inverter. |  |

IV. OPERATION & DISPLAY

4.1 Keypad Control Unit

4.1.1 Operation Panel Instruction

There are two types of keypad control units with YTD-G series inverter (with or without potentiometer), with two kinds of dimensions for each keypad control unit. Refer to Fig 4-1 notes.

4.1.2 Keypad Instruction

Table 4-1       Key Instruction

| Keys | Key Name | Description |
| --- | --- | --- |
|  | “Mode” | Entering the display mode of “function code editing”; To switch for different displays in operation status to reflect various parameters; Press this key in status of amending parameters. Return to display mode of “function code editting” without saving the data amended. |
|  | “Set” | Enter “function-code parameters amending” mode from “function code editting” mode. This key is used for saving data and returning to “function-code editting” mode in the mode of “function-code parameters amending”. |
|  | “Up” | This key is used for data increasing by degrees in the display mode of “function-code editting”, “function-code parameters amending” and frequency display. Step-length of frequency-setting is selected by function code F230, between 0.01～1.00Hz. |
|  | “Down” | This key is used for data decreasing by degrees in the display mode of “function-code editting”, “function-code parameters amending” and frequency display. Step-length of frequency-setting is selected by function code F230 between 0.01～1.00Hz. |
|  | “Run” | To start inverter for operation in keypad control mode (F200＝0). |
|  | “Stop/Reset” | This key is for several purpose: 1): Reset in protection status; 2): Select fuction code among the zone of function codes in display mode of “function-code editting”; 3): Select data-bit while setting parameters; 4): As F201=0, this key can stop inverter in mode of keypad control; As F201=1, this key can stop inverter in mode of keypad control, and has the function of “external emergency stop” in the mode of terminal control and computer remote control; As F201＝2, this key can stop inverter in mode of keypad and terminal 3-line control, direction pulse controlling start/stop, and computer remote control. P lease refer to P26 about the actual “stop” function. |

4.2 Function Parameters Setting

Users can adopt various application modes for changing function-code parameters. Please input user’s password properly in F100 if parameters should be set after it is reconnected to power (user’s password is 8 for manufacturer’s setting or after restoring manufacture’s password). Upon correct input of password, user may change his password again.

Table 4-2             Parameter Setting Steps

| Step | Key | Operation | Display |
| --- | --- | --- | --- |
| 1 |  | Press “Mode” to display function code. |  |
| 2 |  | After Press “stop/reset”, press “▲/▼” for selection of function-code zone; press “▲/▼” to select the function code that need be amended in the selected function-code zone. |  |
| 3 |  | Press “▲/▼” keys for selection of the desired function code. |  |
| 4 |  | Press “set” key to call the data set in function-code. |  |
| 5 |  | Press “stop/reset” keys to select the data bit to be edited. The selected data-bit will flash to indicate that this bit is editable. |  |
| 6 |  | Press “▲/▼” for amending the selected data-bit. |  |
| 7 |  | Press “set” to save data, and return to the present function-code. Press “mode”, then the amended data is invalid, displaying the present function code. |  |

4.3 Function-Codes Grouping

More than 200 function-codes are available, divided into 9 zones, as shown in Fig 4-3.

Fig 4-3     Function-Codes Grouping

| Items | Function-codes | zones |
| --- | --- | --- |
| Basic Parameters | F100～F160 | 1 |
| Operation Control Parameters | F200～F260 | 2 |
| Multi-stage Speed Parameters | F300～F360 | 3 |
| Programmable Input/Output Terminal Parameters | F400～F460 | 4 |
| V/F Control Parameters | F500～F560 | 5 |

Fig 4-3 continued

| Items | Function-codes | zones |
| --- | --- | --- |
| PI Setting Parameters | F600～F660 | 6 |
| Timing & Definable Protection Parameters | F700～F760 | 7 |
| Analog signal Parameters | F800～F860 | 8 |
| Communication Parameters | F900～F960 | 9 |

4.4 Panel Displays

Fig 4-4          Panel Display Items & Descriptions

| Items | Descriptions |
| --- | --- |
| YT-D | It stands for resetting process: inverter will flash the preset frequency afterresetting. |
| 50.00 | Flashing on inverter after connected to power. It is the set frequency for inverter’s running. “▲/▼” keys can set digital setting. |
| 10.00 | Steady display on control panel. It means the inverter’s running frequency or parameter settings. |
| F112 | Function-codes (parameter codes). |
| A 2.5 | It means output current 2.5A. |
| U100 | It means output voltage 100V. |
| L 10.0 | It means linear velocity of 10meters/second. |
| 100 | It implies either rotate speed (100rpm), or count values (100pcs), to be differentiated as per the actual case by users. |
| 1.345 | It means rotate speed (13,450 rpm) |
| OC1、OC2、OC3、OE1 OE2、OE3、OL1、OL2、LU PEr、OH、AdEr、Cb、ESP、ErP、Err | Malfunction Info (refer to Appendix 1). |

V. Function & Parameters Instruction

5.1 Basic Parameters

| F100 User’s Code | Setting Range: 0～9999 | Mfr Value: 8 |
| --- | --- | --- |

● Enter correct user’s password after power connection if you intend to change parameters. Otherwise, parameter setting will not be possible.

● Use may change “user’s password”, same as changing other parameters.

| F102 Inverter’s Rated Current (A) |  | Mfr Value: subject to inverter model |
| --- | --- | --- |
| F103 Inverter Power (KW) | Setting Range: 0.40～75.0 | Mfr Value: power value of this inverter |
| F105 Software Edition No. |  |  |
| F106 Inverter’s Input Voltage Type | Setting Range: 1:single phase 3:three phase | Mfr Value: subject to inverter model |
| F107 Inverter’s Rated Input Voltage(V) | Setting Range: 220 or 380 | Mfr Value: subject to inverter model |

● Preset by manufacturer, used for recording product’ power, corresponding input voltage, rated values and software edition, as info for user.

| F111 Max Frequency (Hz) | Setting Range: F112～400.0 | Mfr Value: 60.00 |
| --- | --- | --- |

● It shows the max frequency for inverter’s operation.

| F112 Min Frequency (Hz) | Setting Range: 0.00～MIN(50.00, F111) | Mfr Value: 0.00 |
| --- | --- | --- |

● It shows the min frequency for inverter’s operation.

● MIN(50.00, F111): it means the lower one of the two values between 50.00 and F111.

e.g.: if F111＝40.00, F112’s setting range will be 0.00～40.00; if F111＝60.00, F112’s setting range will be 0.00～50.00.

| F113 Digital Setting Frequency (Hz) | Setting Range: F112～F111 | Mfr Value: 50.00 |
| --- | --- | --- |

● When inverter frequency-setting mode is “Digital Frequency Setting” (i.e., F204=0 or 1）, frequency can be preset with this function-code. Inverter will automatically run to this frequency after started.

● Frequency can be set by keypad “▲/▼” or “UP” and “DOWN” terminal.

| F114, F116 1st and 2nd Acceleration Time (S) | Setting Range: 0.1～3000 | M fr Value: 20.0 |
| --- | --- | --- |
| F115, F117 1st and 2nd Deceleration Time (S) |  |  |

● “Acceleration Time” refers to the time for inverter to accelerate to the max frequency (F111) from 0Hz; “Deceleration Time” refers to the time for inverter to decelerate to 0Hz from the max frequency (F111).

● When function of programmable input teminal (OP1～OP8) is set to “16 (acceleration/ deceleration time switchover）”, this terminal can be used for switchover of first and second acceleration/ deceleration time. When a low power-level is input into this terminal，inverter will select second acceleration/ deceleration time. Otherwise, first acceleration/ deceleration time shall be default.

| F118 Turnover Frequency（Hz） | Setting Range: 50.00～400.0 | Mfr Value: 50.00 |
| --- | --- | --- |

● Motor’s rated frequency.

● When running frequency is lower than this value, inverter will output constant-torque. When exceeding this value, inverter will output constant power. Normally 50Hz will be selected for turnover frequency.

| F119 Latent Frequency（Hz） | Setting Range: F112～F111 | Mfr Value: 5.00 |
| --- | --- | --- |

● When output frequency exceeds this value; it will be programmed as output status reverse for OUT terminal (or relay terminal) with “Over Latent Frequency” function; in case below this frequency, the terminal will be restored.

| F120 Forward/reverse Switchover Dead-Time（S） | Setting Range: 0.0～3000 | Mfr Value: 2.0 |
| --- | --- | --- |

● This parameter refers to the transition time required during output of 0Hz when inverter change from forward running to reverse running( as shown in Fig 5-1). To set this function may ease the current strike in the course of direction switchover.

● Within “forward/reverse switchover dead-time”, inverter will stop immediately upon receiving “stop” signal.

| F121 Stopping Mode | Setting Range: 0: stop by deceleration time 1: free-stop | Mfr Value: 0 |
| --- | --- | --- |

● “Stop by Deceleration Time” means that motor controlled by inverter will slow down and stop at 0Hz by the set deceleration time.

● “Free Stop” means that after inverter cuts off output upon receiving “stop” instruction, motor will run freely and stop by inertia. “Free Stop” mode will be selected by function-code F700 (0: free stop immediately 1: delayed free stop) and F701 (Delay time of Free-Stop and Programmable Output Terminal’s Action ).immediately 1: delayed free stop) and F701 (Delay time of Free-Stop and Programmable Output Terminal’s Action ).

| F122 Reverse Running Forbidden | Setting Range: 0:null 1: valid | Mfr Value: 0 |
| --- | --- | --- |

● This function may avoid damage on equipment due to mis-operation causing motor-reverse running.

| F124 Jogging Frequency (Hz) | Setting Range: F112～F111 | Mfr Value: 5.00 |
| --- | --- | --- |
| F125 Jogging Acceleration Time(S) | Setting Range: 0.1～3000 | Mfr Value: 20.0 |
| F126 Jogging Deceleration Time (S) |  |  |

● Jogging function only applies to teminal control mode (F200＝1).

● Jogging operation can be realized by connected CM with the programmable input terminal (OP1～OP8) defined as jogging function.

| F127, F129 Skip Frequency A,B (Hz) | Setting Range: 0.00～F111 | Mfr Values: 0.00 |
| --- | --- | --- |
| F128, F130 Skip Width A,B (Hz) | Setting Range: 0.00～5.00 | Mfr Values: 0.00 |

● Systematic vibration may occur when the motor is running at a certain frequency. This parameter is set to skip this frequency.

● The inverter will skip the point automatically when output frequency is equal to the set value of this parameter.

● “Skip Width” is the span from the upper to the lower limit around Skip Frequency.

● As shown in Fig 5-3: Skip Frequency=20Hz, Skip Width=5.00, inverter will skip automatically when output is between 17.5～22.5Hz.

| F131 Displays | Setting Range: 1～127 1: Frequency 2: Rotate Speed 4:Count Values 8: Output Current 16: Function-Code Editing 32:Output Voltage 64:Linear Velocity 127: Display All | Mfr Values: 127 |
| --- | --- | --- |
| Display | Indication | Unit |
| Frequency | 50.00 | Hz |
| Rotate Speed | 300 | rpm |
|  | 1.345 | 10,000 rpm |
| Count Value | 99 |  |
| Output Current | A 3.5 | Ampere |
| Function-Code Editing | F112 |  |
| Output Voltage | U100 | Volt |
| Linear Velocity | L7.85 | meter/second |

● Selection of any value from 1, 2, 4, 8, 16, 32 and 64 shows that only one specific display item is selected. Should multiple display items be intended, add the values of the corresponding display items and take the total values as the set value of F131, e.g., just set F131 to be 25 (1+8+16) if you want to call “frequency”, “output current” and “function-code editing”. The other display items will not appear.

● As F131＝127, all display items are visible, of which, “function-code editing” will be visible whether or not it is selected.

● Should you intend to check any display item, just press “mode” for switchover.

● Refer to the right table for each specific physical unit and its indication:

| F132 Number of motor pole pairs | Setting Range: 1～6 | Mfr Value: 2 |
| --- | --- | --- |
| F133 Driven system’s drive ratio | Setting Range: 0.1～100.0 | Mfr Value: 1.0 |
| F134 Transmission-wheel radius (m) | Setting Range: 0.001～1.000 | Mfr Value: 0.001 |

● Calculation of retoting speed and linear velocity:

If inverter’s max frequency F111＝50.00Hz, number of motor pole pairs F132＝2，drive-ratio F133＝1.0，Transmission-wheel radius F134＝0.05m, then

Transmission-wheel perimeter: 2πr =2×3.14×0.05=0.314 (meter)

Transmission shaft rotate speed: ［60× operation frequency/(number of pole pairs × drive ratio)］×(1-0.03)=60×50/(2×1.00)×(1-0.03)=1455rpm(0.03: slip ratio)

Final linear velocity:rotatespeed×perimeter=1455×0.314456.87(meter/minute)＝7.61(meter/second)

| F139 whether to start automatically after reconnection to power or malfunction | Setting Range: 0: null 1: valid | Mfr Value: 0 |
| --- | --- | --- |

● This function means that inverter is reconnected after power disconnection or whether it can be started automatically after malfunction protection. If inverter is selected “null”, it shall start to operate only after receiving “run” signal.

● After auto start by inverter, F705 and F706 shall set the times and intervals for auto-start.

● This function only applies to control modes of keypad control (F200＝0) , 3-line control (F200＝1, F208＝2 or 3) and direction-pulse controlled start/stop (F200＝1 and F208＝4).

| F160 Reverting to manufacturer values | Setting Range: 0:Not reverting to manufacturer values; 1：Reverting to manufacturer values | Mfr Value: 0 |
| --- | --- | --- |

● Set F160 to 1 when there is disorder with inverter’s parameters and manufacturer values need to be restored.

● After “Reverting to manufacturer values” is done, F160 values will be

automatically changed to 0.

● “Reverting to manufacturer values”will not work for the function-codes marked “○”in the “Note” column in the Appendix 2 Function-Code Zoom Table.

5.2 Operation Control Parameters

| F200 Operation Control | Setting Range: 0: Keypad Control/485Communication Control 1: Terminal Control 2: Computer Remote Control | Mfr Value: 0 |
| --- | --- | --- |

● “Keypad Control/485Communication Control” means that inverter’s running is controlled by keypad or control box connected by 485-communication interface. Motor’s rotate-direction is set by F207.

● “Terminal Control”shall control inverter’s operation through programmable input terminal named with “FWD”, “REV”and “X” functions (OP1～OP8). Four control modes are available in mode of terminal control. Refer to function-code F208.

● “Computer Remote Control” means that computer will control inverter’s operation through 485-communication interface.

| F201 Key Functions | Setting Range: 0: valid only in mode of keypad control 1: valid in any modes 2: valid at time of keypad, terminal 3-line control, controlling start/stop by direction pulse and computer remote control | Mfr Value: 0 |
| --- | --- | --- |

● As F201＝0, and in mode of keypad control, press this key during running, inverter will stop by deceleration time.

● As F201＝1, and in mode of keypad control, press this key during running, inverter will stop by deceleration time; in mode of terminal control or computer remote control, press this key during running, inverter will stop. Meanwhile, keypad control unit will display error signal “ESP”.

● As F201＝2, this key will work in modes of keypad, terminal 3-line control, start/stop controlld by direction-pulse, code-timing and computer remote control. Press this key during running, inverter will stop by deceleration time.

● As inverter is having stalling operation, press this key during running, inverter will stop. Meanwhile, keypad control unit will display error signal “ESP”.

| F204 Basic Speed ControlModes | Setting Range: 0: setting digital frequency, setting keypad and terminal UP and DOWN, not saving result when power off. 1: setting digital frequency, setting keypad and terminal UP and DOWN, saving result when power off. 2: Multi-Speed control. 3: Analog Channel 1（V2）Speed control. 4: Analog Channel 2（I2）Speed control. 5: Analog Channel Compound Speed-Control 1: k1×V2+k2×I2( of which, “V2” and “I2”implies the analog signal input by Analog Channel V2 and I2). 6: Analog Channel Compound Speed-Control 2: k1×V2－k2×I2（Same as above with “V2” and “I2”）. 7: Speed control set by pulse frequency. 8: Code Speed Control means inverter is run by various switching status combination of terminals OP1～OP8. 9: Analog Channel Compound Speed-Control 3: k1×V2＋k2×（I2－5V）. 10: Keypad potentiometer speed-control selection:Single-phase inverters without internal braking resistor and three phase 11~110KW inverters have this function. | Mfr Value:0 |
| --- | --- | --- |

● Multi-stage speed control includes multi-stage speed running, automatic circulating running and 8-stage speed running, to be selected by function-code F210 (P29). Running frequency of stage speed can be adjusted with keypad “▲/▼” keys or “UP” and “DOWN” terminals The result of frequency adjusting is unsaved when power off. Refer to 5.3 Multi-stage Speed Parameters for relevant function parameters setting.

● In case of speed control with analog signal, please set F800, F801, F807 and F808 (P41) according to the input of actual analog signal and frequency setting requirements. Meanwhile, select the input analog type through jumper terminal. Input analog will set inverter’s running frequency or PI adjusting.

● Speed-control set by pulse-frequency means that inverter will be controlled through pulse-frequency input by OP1 terminal (F408=23) from peripheral equipment. Refer to F809 and F810 (P45) for relevant function parameters.

● In case of code speed-control, frequency will be set by input terminal programmed with code speed control function (this terminal function is defined as 18): Code Speed-Control Frequency＝binary-digit of terminal-input＊max frequency/255 While using code speed control, input terminal function of input terminal OP1～OP8 can be redefined.

● Refer to 6.2 Speed Control Mode for various speed control modes.

Use of Jumper Terminal

Near control terminal,there is a jumper terminal SW1.T he jumper terminal use for choosing analog input voltage 0~5V or 0~10V.Control terminal VCC supply user with +5V source to use.

| F207 Keypad Direction Set | Setting Range: 0:forward; 1:reverse | Mfr Value: 0 |
| --- | --- | --- |

● In mode of keypad control (F200＝0), set motor’s running direction.

| F208 Terminal Control Mode | Setting Range: 0: two-line type 1 1:two-line type 2 2: three-line type 1 3:three-line type 2 4:start/stop controlled by direction pulse | Mfr Value: 0 |
| --- | --- | --- |

● Five modes are available for terminal operation control. As shown in Table 5-1, “    ”stands for switch-on, “   ” for normally closed contact, “   ” for normally open contact. “FWD”, “REV” and “X” are three terminals designated in programming OP1～OP8.

Table 5-1          Terminal Control Mode

| F208 | Terminal Function Realised and Control-Loop Wiring |
| --- | --- |
| 0: two-line type 1 forward/stop reverse/stop |  |
| 1: two-line type 2 reverse/forward running/stop |  |
| 2: three-line type 1 forward running/stop reverse running/stop |  |
| 3:three-line type 2 forward running/stop reverse running/stop |  |
| 4: start/stop controlled by direction impulse. forward running/stop reverse running/stop |  |

| F209 Stage-Speed Changing Control | Setting Range: 0: adjusting stage-speed forbidden 1: adjusting stage-speed allowed | Mfr Value: 0 |
| --- | --- | --- |
| F210 Stage-Speed Types | Setting Range: 0: multi-stage speed running 1:Auto circulating running 2: 8-stage speed running | Mfr Value: 0 |

| F211 Auto Circulating Running Speed Selection | Setting Range: 2～7 | Mfr Value: 7 |
| --- | --- | --- |
| F212 Auto Circulating Running Times Selection | Setting Range: 0～9999 | Mfr Value: 0 |
| F213 Free Running Selection after Auto Circulating Running | Setting Range: 0: stop 1: keep running at last stage speed | Mfr Value: 0 |

● Stage-Speed change control means whether keypad “▲/▼”keys or “UP” and “DOWN” terminals will be used during multistage speed running to adjust the present running speed. F230 (P31) sets step-length for each adjusting. This setting will not change function-code parameters, and will not be saved in memory when power disconnected. Parameters set by function-code will therefore be called for multistage speed frequency again when power reconnected.

●“Once” means auto circulating running at all fixed stage speeds for one time.

● If F212＝0, inverter will keep circulating running until it is stopped by “stop signal”.

● If F212>0, inverter will finish auto circulating running in the mode set by F213 after inverter makes circulating running for the fixed times ( to be set by F212): if F213=0, then it will stop; if F213=1, then running will be kept at the last speed.

e.g.: F211=3, F212=100, F213=1, select auto circulating running at 3 speeds for 100 times. After auto circulating running, keep running at 3rd speed.

| F214 k1 | Setting Range: 0.0～10.0 | Mfr Value: 1.0 |
| --- | --- | --- |
| F215 k2 | Setting Range: 0.0～10.0 | Mfr Value: 1.0 |

● k1 and k2 are proportion parameters in case of (F204=5, 6, 9). When compound speed control, the actual value of input analog will be the product of set value for peripheral equipment and proportion parameters.

e.g. when k1＝0.5, k2＝2.0, scope for analog which is input into inverter through V2 channel is 0.0～5.0V; scope for analog which is input into inverter through I2 channel is 0.0～20.0V.

| F216 Stage-speed Running Changing Storage Selection | Setting Range: 0: Storage; 1:No Storage | Mfr Value: 1 |
| --- | --- | --- |
| F221 Count Frequency Divisions | Setting Range: 1～1000 | Mfr Value: 1 |
| F222 Set Count Times | Setting Range: F224～9999 | Mfr Value: 1 |
| F224 Designated Count Times | Setting Range: 1～F222 | Mfr Value: 1 |

● Count frequency divisions refer to the ratio of actual pulse input and inverter’s count times, i.e.,

Inverter’s Count Times ＝

e.g. when F221＝3, inverter will count once for every 3 inputs of external impluse.

● Set count times refer to a count width pulse output by the output terminal (OUT terminal or relay) programmed with “reaching the set count times”function when a certain number of pulses are input from OP1. Count will restart after the count value reaches “fixed times”.

As shown in Fig 5-6: if F221=1, F222＝8, F417＝7, OUT will output an instruction signal when OP1 inputs the 8th pulse.

● Designated count times refer to an pulse output by the output terminal (OUT or RELAY terminal) programmed with “reaching the set count times”function when a certain number of pulses are input from OP1, until count value reaches the “set times”.

As shown in Fig 5-6: if F221=1, F224＝5, F222＝8, F416＝8, relay will output an instruction signal when OP1 inputs the 5th pulse, relay will output an instruction signal until reaching “fixed count times 8”.

1      2     3      4      5      6     7      8      1

OP1 Input:

OUT:

Relay:

| F230 Frequency Setting Step length (Hz) | Setting Range: 0.01～1.00 | Mfr Value: 0.01 |
| --- | --- | --- |

● This parameter means the changing frequency value when adjusting “▲/▼” keys once or press “UP” and“DOWN” terminal once.

5.3 Multistage Speed Parameters

| F300, F306, F312, F318, F324, F330, F336 Stage-Speed Running Direction | Setting Range: 0: Forward; 1: Reverse | Mfr Value: F300＝0 F306＝1 F312＝0 F318＝1 F324＝0 F330＝0 F336＝0 |
| --- | --- | --- |

● Running direction will be provided for each speed.

● When keypad control/485 communication control (F200＝0) or computer remote control (F200＝2), stage-speed running direction will be set by the above function-code; when controlled by terminal (F200＝1), stage-speed running direction will be controlled by the input terminal defined with “FWD”, “REV” and “X” functions (See Table 5-2).

| F301, F307, F313, F319, F325, F331 and F337 Stage-Speed Acceleration time (S) F304, F310, F316, F322, F328, F334 and F340 Stage-Speed Deceleration time(S) | Setting Range: 0.1～3000 | Mfr Value: 20.0 |
| --- | --- | --- |

● Acceleration time and deceleration time will be provided for each speed.

| F302, F308, F314, F320, F326, F332 and F338 Stage-Speed Running Frequency (Hz) | Setting Range: F112～F111 | Mfr Value: F302＝5.00 F308＝10.00 F314＝15.00 F320＝20.00 F326＝25.00 F332＝30.00 F338＝35.00 |
| --- | --- | --- |

● Running frequency for each speed will be provided.

● In case of multistage speed control, speed control is allowed for running frequency of stage-speed by using “▲/▼” keys or “UP” and “DOWN” terminals.

| F303, F309, F315, F321, F327, F333 and F339 Stage-Speed Running Time(S) | Setting Range: 0.1～3000 | Mfr Value: 20.0 |
| --- | --- | --- |

● Running time will be provided for each speed.

● When auto circulating running (F210＝ 1), stage-speed running time will be set by the above function-codes: In case of multistage running (F210＝0) or running at 8th speed (F210＝2), it will be running at stage-speed and peripheral equipment control will be stopped. Therefore It is not restricted by stage-speed running time.

| F305, F311, F317, F323, F329, F335, F341 Stage-Speed Stop/Waiting Time(S) | Setting Range: 0.0～3000 | Mfr Value: 0.0 |
| --- | --- | --- |

● Stop/waiting time will be provided for each speed.

● When auto circulating running (F210＝1), inverter will use stage-speed stop/waiting time; in case of multistage running (F210＝0) or running at 8th speed (F210＝2), it will be running at stage-speed and peripheral equipment control will be stopped. It is therefore not restricted by stage-speed stop/waiting time.

| F342 Selection of Compound Speed Control for Stage-Speeds | Setting Range: 0: not allowed 1: allowed | Mfr Value: 0 |
| --- | --- | --- |
| F343 Selection of Compound Speed Control Mode for Stage-Speeds | Setting Range: 0: multi-stage running frequency + values set for F344 1: Multi-stage running frequency + I2 channel analog values | Mfr Value: 0 |
| F344 Digital Frequency Setting for Stage-Speed Compound Speed Control（Hz） | Setting Range: 0.00～20.00 | Mfr Value: 0.00 |

● Compound speed control for stage-speeds can be controlled together by multi-stage speed control, digital speed control and analog speed control. This speed control mode only works for multi-stage and 8-stage running, not for automatic circulating running, i.e., such condition must be met as F210＝0 or 2 when selecting compound speed control.

● F343＝0, select the control mode both by multistage speed control and digital speed control. The running frequency at each speed will then be the sum adding multistage speed frequency and set values of digital frequency. Set values of digital frequency will be set by F344.

e.g. the values set for current running frequency for each stage speed: F302＝5.00, F308＝10.00, F314＝ 15.00, F320＝20.00, F326＝25.00, F332＝30.00, F338＝35.00. To set F344＝10.00, running frequency for each stage speed in case of compound speed control: F302＝15.00，F308＝20.00，F314＝25.00，F320＝30.00，F326＝35.00，F332＝40.00，F338＝45.00.

● F343＝1, select the control mode both by multistage speed control and analog speed control. The running frequency at each speed will then be the sum adding multistage speed set frequency and I2 channel analog values. Analog value set for I2 is 0～10V (to be provided by peripheral equipment through I2 channel), corresponding frequency 0～10Hz.

e.g., the values set for running frequency at each speed: F302＝5.00, F308＝10.00, F314＝15.00, F320＝20.00, F326＝25.00, F332＝30.00 and F338＝35.00. If the values set for “I2” channel analog is 5.0V, running frequency at each speed at time of compound speed control: F302＝10.00，F308＝15.00，F314＝20.00，F320＝25.00，F326＝30.00，F332＝35.00，F338＝40.00.

5.4 Programmable Input & Output Terminal Parameters

5.4.1 Programmable Input Terminal

| F408 ～ F415 Terminal Function Definition | Setting Range: 0～23 | Mfr Value: F408＝9; F409＝1; F410＝2; F411＝3; F412＝7; F413＝13; F414＝14; F415＝4 |
| --- | --- | --- |

● Terminal function OP1～OP8 will be defined separately. 22 functions can be available for each terminal.

Table 5-2        Programmable Input Terminal Function

| F408～F415 | Description | Remarks |
| --- | --- | --- |
| 0 | No Function |  |
| 1 | Multi-Speed Terminal1 | Used in defining multi-speed function, refer to 6.2 Speed Control Mode for multi-speed control. |
| 2 | Multi-Speed Terminal 2 |  |
| 3 | Multi-Speed Terminal 3 |  |
| 4 | Reset | When malfunction protection occurs, this terminal is connected with CM, which will reset converter. |
| 5 | Free-stop | During it’s working，this terminal is connected with CM, which will bring converter to free stop. |
| 6 | Reserved |  |
| 7 | External Emergency Stop | The inverter will stop output immediately if it receives “external emergency stop”signal during running. “ESP” malfunction signal will be displayed in the meanwhile. Resetting will be possible after signal of “external emergency stop” is released. |
| 8 | Acceleration/Deceleration Prohibited | During acceleration/deceleration, this terminal works (i.e. this terminal is connected CM). Inverter stops acceleration/ deceleration，and keeps the present running frequency, this terminal does not work（i.e.this terminal breaks up with CM）, acceleration/deceleration process will continue. |
| 9 | Jogging Forward Running JOGF | Connecting terminal with CM could make jogging forward running. |
| 10 | Jogging reverse running JOGR | Short circuit of this terminal with CM could make jogging reverse running. |
| 11 | Frequency Increasing by Degrees UP | This terminal is equal to the “▲” key on the operation panel. |
| 12 | Frequency Decreasing by Degrees DOWN | This terminal is equal to the “▼” key on the operation panel. |
| 13 | “FWD”Terminal | Control terminal for inverter terminal running. Refer to Table 5-2 for terminal control mode. |
| 14 | “REV” Terminal |  |
| 15 | Three-line Type, Input Terminal of “X” | One terminal of the three-line control mode, used to stop inverter. |

Table 5-2 continued

| F408～F415 | Description | Remarks |
| --- | --- | --- |
| 16 | Switchover of Acceleration/Deceleration Time | Used in switchover of the first and the second acceleration /deceleration times. When this terminal is working (i.e.it is connected with CM), the second acceleration/deceleration time is carried out. When this terminal is not working (i.e. it is disconnected with CM), then the first acceleration/deceleration time is used. |
| 17 | Peripheral Equipment Malfunction | The inverter will stop output immediately and display “ErP”if it receives the terminal input signal of “peripheral equipment malfunction” during operation. Resetting will not be done until the signal of “peripheral equipment malfunction” is released. |
| 18 | “Coding Speed Control” Input Terminal | When this function is selected，OP1～OP8 will be binary digital input terminal. OP1 terminal corresponds to low bit of the binary digit while OP8 corresponds to high bit of the binary digit, and by analogy. Set to 1 when the terminals of the corresponding position is working; otherwise reset to 0. |
| 19 | Close Loop Switched to Open Loop | Switch the speed control mode PI to that of F204: When the function terminal is open circuit with CM, it will be controlled by the close loop. When it is connected with CM, by open loop. |
| 20 | Compound Channel Speed Control Switched to Single Channel Speed Control | Realize the switchover between compound speed control and single-channel analog speed control (default: V2 channel). |
| 21 | Terminal Counting | Input of count pulse of the built-in counter. |
| 22 | Count Value Reset to Zero | Reset the terminal count value to zero. |
| 23 | Pulse Frequency Input Terminal (Only valid for OP1) | When F408＝23，set the speed with the external input pulse. Max frequency of the pulse input: 9999Hz. |

Warning: 1. The count pulse frequency of the input terminal must not exceed 300Hz. Otherwise the counter error will appear.

2.Terminal functions are not allowed for redefination except for coding speed control.

5.4.2 Programmable Output Terminal

| F416 Relay Output | Setting Range：0～13 | Mfr Value:1 |
| --- | --- | --- |
| F417 OUT Terminal Output |  | Mfr Value:4 |

● Programmable output terminal includes collector open-circuit output terminal OUT and relay output terminals TA, TB and TC.

● The output terminal “action” in the following table refers to the relay sucking: TA closes TC, TB disconnects TC disconnection, OUT terminal is on status with low resistance.

Table 5-3     Programmable Output Terminal Function

| F416, F417 | Description | Remarks |
| --- | --- | --- |
| 0 | No Function |  |
| 1 | Inverter Malfunction Protection | This terminal will be “action” when inverter has malfunction protection except for undervoltage protection. |
| 2 | Over Latent Frequency | This terminal will be “action” when running frequency exceeds the set value of F119 (P23). This terminal will restore when running frequency is lower than the value. |
| 3 | Free Stop | The terminal will be “action” when signal of “free stop” is input. |
| 4 | Inverter in Operation | The terminal will be “action” when inverter works. And it will restore when inverter stops. |
| 5 | During DC Braking | The terminal will be “action” when inverter is under DC braking. |
| 6 | Indicating Switchover of Acceleration / Deceleration | This terminal will be “action” when it carries out the instruction of “switchover of acceleration/deceleration”. |
| 7 | Reaching the Set Count Value | This terminal will be “action” when inverter carries the external count instruction and count value reaches the set value of F222 . |
| 8 | Reaching the Designated Count Value | This terminal will be “action”when inverter carries the external count instruction and count value reaches the set value of F224. |
| 9 | Overload Early Warning Signal | This terminal will be “action” and send a signal of overload protection early warning when the current reaches a certain value. |
| 10~13 | Reserved |

5.4.3 Analog signal Output Terminal

| F418 FM Output Function Selection | Setting Range: 0: indicate output frequency value 1: indicate output current value | Mfr Value:0 |
| --- | --- | --- |

● When selecting “indicate output frequency”, 0～10V output corresponds to 0～F111 (max frequency).

● When selecting “indicate input frequency”, 0～10V output corresponds to 0～Ie（inverter’s rated current）.

| F419 FM Output Calibration（%） | Setting Range: 0～200 | Mfr Value:100 |
| --- | --- | --- |

● This function is used to calibrate the output error of FM. Calibration value will be subject to the actual measuring.

| F420 IM(FM)Output Range Selection | Setting Range: 0: 0～20mA (0～10V) 1: 4～20mA (2～10V) | Mfr Value: 0 |
| --- | --- | --- |

● Proper selection of current output range (voltage) will be subject to different types of meters.

5.5 V/F Control Parameters

5.5.1   V/F Compensation & Carrier Wave Frequency

| F500 Slip Compensation | Setting Range: 0.00～0.08 | Mfr Value: 0.03 |
| --- | --- | --- |

● Slip will gain in case of higher overload. Adjusting the parameter of F500 will make motor’s actual otate-speed close to the rated rotate-speed.

| F501 V/F Curve Control Mode | Setting Range: 0: beeline 1:polygonal line 2:square | Mfr Value: 0 |
| --- | --- | --- |
| F502 Torque Promotion（％） | Setting Range:1～MIN（15，F506） | Mfr Value: 5 |

● This product has 3 control modes for “V/F” curve, to promote output torque at low frequency.

● Torque promotion can be set through F502 for selection of polygonal-line type V/F curve. Higher value setting will incur bigger compensation (as shown in Fig 5-7)，and more starting current. Over-setting values may result in inverter’s over-current protection.

● Square V/F curve will meet requirements where blower and pumps are used.

● User may select polygonal-line type V/F curve for flexible setting if he has any special requirements for V/F curve.

● MIN(15, F506) refers to the smaller one of the two set values between 15 and F506.

| F505 User-Defined Frequency Point 1 (Hz) | Setting Range: F112～F507 | Mfr Value:10.00 |
| --- | --- | --- |
| F506 User-Defined Voltage Point 1 (％) | Setting Range: F502～MIN(100, F508) | Mfr Value: 30 |
| F507 User-Defined Frequency Point 2 (Hz) | Setting Range: F505～F118 | Mfr Value: 20.00 |
| F508 User-Defined Voltage Point 2 (％) | Setting Range: F506～MIN(100, F509) | Mfr Value: 40 |
| F509 Voltage Corresponding Turnover Frequency（％） | Setting Range: F508～100 | Mfr Value: 100 |

● User may define on its own polygonal-line type V/F curve as per its requirements and actual load, as shown in Fig 5-8.

● MIN(100, F508) shows the smaller of the two set values between 100 and F508.

| F511 Auto Voltage adjusting | Setting Range: 0: no adjusting 1: adjusting | Mfr Value: 0 |
| --- | --- | --- |

● In case of fluctuation with input voltage, this function may automatically adjust ratio of PWM output to keep output voltage stable.

| F512 Carrier-Wave Frequency Setting (kHz) | Setting Range: 1～values set as per inverter model | Mfr Value: subject to inverter model |
| --- | --- | --- |

● Carrier-wave frequency is modulating-frequency when inverter outputs PWM wave.

● Promoting carrier-wave may improve output current-waveform, reduce motor noise, but the temperature of inverter will rise.

| F513 Random Carrier-Wave Selection | Setting Range: 0: not allowed 1: allowed | Mfr Value: 1 |
| --- | --- | --- |

● F513＝0: inverter will modulate as per the carrier-wave set by F512;

● F513＝1: inverter will operate in mode of random carrier-wave modulating, which will reduce noise effectively.

5.5.2 Braking Parameters

| F514 DC Braking Function Selection | Setting Range: 0: not allowed 1:braking during start 2:braking during stop 3:braking during start+stop | Mfr Value:0 |
| --- | --- | --- |
| F515 Initial Frequency of DC Braking (Hz) | Setting Range: 0.00～5.00 | Mfr Value: 5.00 |
| F516 DC Braking Current (%) | Setting Range: 0～150 | Mfr Value: 100 |
| F517 Braking Lasting Time During Starting (S) | Setting Range: 0.0～10.0 | Mfr Value: 5.0 |
| F518 Braking Lasting Time During Stopping (S) | Setting Range: 0.0～10.0 | Mfr Value: 5.0 |

● In case of negative torque, using “pre-starting braking” may ensure that motor stays in quiescence before starting.

● Parameters related to “DC Braking”: F515, F516, F517 and F518, with following interpretations:

a. F515: Initial-frequency of DC-braking. DC braking will start when inverter’s output frequency is lower than this value.

b. F516: DC braking current. The ratio of current and rated current in case of

braking. The higher this value is, the higher braking torque is.

c. F517: Braking lasting time when starting. The lasting time of DC braking before inverter starts.

d. F518: Braking lasting time when stopping. The lasting time of DC braking in course of inverter’s stopping.

● DC braking, as shown in Fig 5-9.

| F519 Energy Consumption Brake Ratio (%) | Setting Range: 0～100 | Mfr Value: 50 |
| --- | --- | --- |

● It means the ratio when power resistor is used in energy consumption braking. Higher value will lead to quicker energy consumption with motor feedback, which can effectively shorten inverter’s deceleration time.

5.5.3 Stalling Adjusting

| F525 Stalling Adjusting Function Selection | Setting Range: 0:not allowed 1: allowed | Mfr Value: 0 |
| --- | --- | --- |
| F526 Stalling Current Adjusting (%) | Setting Range: 120～200 | Mfr Value: 160 |
| F527 Stalling Voltage Adjusting (%) | Setting Range: 120～200 | Mfr Value: 140 |

● Inverter automatically stops acceleration/deceleration at stalling, and will go on with acceleration /deceleration after output current or bus voltage drops. Stalling adjustment can avoid trip as inverter is accelerating / decelerating.

● Set stalling voltage properly for inverters without energy consumption resistor or braking unit to avoid over-voltage trip.

5.6 PI Adjusting Parameters

| F600 PI Adjusting Function Selection | Setting Range: 0:not allowed 1: allowed | Mfr Value: 0 |
| --- | --- | --- |
| F601 PI Adjusting Channel Setting Selection | Setting Range: 0: Digital Setting 1:V2 Channel Setting 2: I2 Channel Setting | Mfr Value: 0 |
| F602 PI Adjusting Digit Setting (V) | Setting Range: 0.00～10.00 | Mfr Value: 5.00 |
| F603 PI Adjusting Feedback Channel Selection | Setting Range: 0:V2 channel feedback 1:I2 channel feedback 2:OP1 pulse channel feedback | Mfr Value: 0 |

● Digit given is a target value (0～10V) for PI adjusting set by function code F602.

● Analog given (or feedback) will be achieved through analog channelV2 and I2 together with jumper teminal, including voltage analog and current analog. Refer to Use of Jumper Terminals for detailed operation;

● Pulse channel feedback means taking the pulse frequency input by terminal OP1 as feedback (F408=23).

| F604 Min Analog Set by PI (V) | Setting Range: 0.00～F606 | Mfr Value: 0.00 |
| --- | --- | --- |
| F605 Corresponding Feedback for Min Analog Set by PI (V) | Setting Range: 0.00～10.00 | Mfr Value: 0.00 |
| F606 Max Analog Set by PI (V) | Setting Range: F604~10.00 | Mfr Value: 10.00 |
| F607 Corresponding Feedback for Max Analog Set by PI (V) | Setting Range: 0.00～10.00 | Mfr Value: 10.00 |

● Set F604～F607 as per the setting value scope and feedback scope of the close-loop adjusting system, as well as interrelation between setting value and feedback value. Normally setting is done as per the corresponding relation between setting and feedback meter.

● If thermo-regulation is made, regulation range is 20～100℃ and setting range of the corresponding control system is 2～8V, and when temperature fluctuates within 20～100℃ and output range of temperature measurement meter is 3～9V, then F604～F607 is set as follows:

F604=2.00, F606=8.00; F605=3.00, F607=9.00.

| F608 Proportion Gain | Setting Range: 1～1000 | Mfr Value: 100 |
| --- | --- | --- |
| F609 Integration Time (S) | Setting Range: 0.1～10.0 | Mfr Value: 0.1 |
| F610 Sampling Cycle (S) | Setting Range: 0.1～10.0 | Mfr Value: 0.1 |

● Proportion Gain (P) and Integration Time (Ti) as shown in Fig 5-10. Sampling Cycle refers to that of feedback quantity x. Ti as shown here refers to Integration Time. The bigger Ti is, the slower the system responds; the smaller Ti is, the faster the system responds, but it is to surge. Contrariwise with Proportion Gain (P).

| F611 PI Adjusting Accuracy (%) | Setting Range: 0～20 | Mfr Value: 5 |
| --- | --- | --- |

● It refers to the percentage of the deviation (between feedback of PI regulation and setting value) against close-loop given value. Deviation range allowed by PI regulation is shown in Fig 5-11.

| F612 PI Regulating Polarity | Setting Range: 0: negative feedback adjusting 1: positive feedback adjusting | Mfr Value: 0 |
| --- | --- | --- |

● Negative feedback adjusting means that when regulation deviation is positive, PI adjusting will bring output frequency down.

● Positive feedback adjusting means that when regulation deviation is positive, PI adjusting will bring output frequency up.

5.7 Timing Control & Definable Protection Parameters

5.7.1 Timing Control

| F700 Mode Selection for Free-Stop | Setting Range: 0:Stop immediately 1:Stop Delay | Mfr Value: 0 |
| --- | --- | --- |
| F701 Delay time of Free-Stop and Programmable Output Terminal’s Action (S) | Setting Range: 0.0～60.0 | Mfr Value: 0.0 |

● “Immediate Stop” means that inverter will stop output immediately when detecting “free stop” signal, and load will stop by inertia.

● “Delayed Stop” means that inverter will execute “free stop” command after waiting some time upon receiving “stop” instead of stopping immediately. Delay time is set by F701.

| F702 Fan Control Selection (valid only for 18.5～110KW inverter) | Setting Range: 0: temperature controlled fan running 1: not temperature controlled fan running | Mfr Value: 0 |
| --- | --- | --- |

● As F702＝0, fan is controlled by radiator’s temperature during running. It will start to work when temperature reaches a certain value;

● As F702＝1, fan is controlled by radiator’s temperature during running, i.e., fan will start to work when inverter is power connected.

| F705 Allowed Auto-restart Times | Setting Range: 0～5 | Mfr Value: 3 |
| --- | --- | --- |
| F706 Interval Time of Auto-restart(S) | Setting Range: 0.0～10.0 | Mfr Value:3.0 |

● When auto start is working, i.e., F139＝1, set the times allowed for auto restart and interval time of start after inverter is power-reconnected or malfunction protection.

5.7.2 Settable Protection－Under-Voltage Protection and Overloading Protection

| F709 Under-Voltage Protection Value (V) | Setting Range: 200～420 | Mfr Value: subject to inverter’s model |
| --- | --- | --- |

● As bus-voltage is lower than this set value, inverter will start undervoltage protection.

| F715 Overloading Adjusting Gains | Setting Range: 0～1000 | Mfr Value: Adjusting value |
| --- | --- | --- |
| F716 Inverter Overloading Coefficient (％) | Setting Range: 150～180 | Mfr Value: Adjusting value |
| F717 Motor Overloading Coefficient (％) | Setting Range: 20～120 | Mfr Value: Adjusting value |

● As output current is accumulated to overloading protection value, inverter will start “overloading protection”.

● Overloading Adjusting Gains (F715): the time constant of the response speed of overload protection, which is used to regulate the speed of frequency decreasing. The bigger gains are, the slower frequency decrease.

● Inverter Overloading Coefficient (F716): the ratio of overload-protection current and rated current when overload protect occurs. Its value shall be subject to actual load.

● Motor Overloading Coefficient (F717): Set as follows in order to protect motor when inverter is running with lower-power motor:

Motor Overloading Coefficient ＝                     ×100％

5.7.3 Trouble Recording

| F720 Third Malfunction Type By Counting Down | 0: No Trouble 1: Acceleration Over-Current 2: Deceleration Over-Current 3: Constant-Speed Over-Current 4: Acceleration Over-Voltage 5: Deceleration Over-Voltage 6: Constant-Speed Over-Voltage 7: Undervoltage 9: Inverter Overload 10: Motor Overload 11: Excess Temperature 12: User’s Password Error／Serious Exterior Interference 13: Out-Phase 15: Emergency Stop 19: Galvanoscopy Error 21: Peripheral Equipment Malfunction |
| --- | --- |
| F721 Second Malfunction Type By Counting Down |  |
| F722 The Latest Malfunction Type |  |
| F723 The Latest Malfunction Frequency (Hz) |  |
| F724 The Latest MalfunctionCurrent (A) |  |
| F725 The Latest MalfunctionVoltage (V) |  |

● F720～725 is used to record the latest three malfunction types and the corresponding frequency, current and voltage at last malfunction. Refer to Appendix 1 for causes and countermeasures for any malfunction.

5.8 Analog signal Parameters

5.8.1 Analog signal Input

In mode of analog speed control, it is necessary to set the min and max input analog, and the corresponding output frequency to secure a good speed control effect.

| F800 Min Analog Input (V) | Setting Range: 0.00～MIN(F801,10.00) | Mfr Value: 0.00 |
| --- | --- | --- |
| F801 Max Analog Input (V) | Setting Range: MAX（0.00，F800）～10.00 | Mfr Value: 10.00 |
| F807 Corresponding Frequency for Min Analog (Hz) | Setting Range: F112～F111 | Mfr Value: 0.00 |
| F808 Corresponding Frequency for Max Analog (Hz) | Setting Range: F112～F111 | Mfr Value: 50.00 |

● Set min and max analogs as per actual input range of analog signal.

● The setting values of F807 and F808 decide proportion mode of analog adjustment change, as shown in Fig5-12:

● MIN (F801, 10.00) refers to the smaller one of the two values between F801 setting value and 10.00.

● MAX (0.00, F800) refers to the bigger one of the two values between F800 setting value and 0.00.

5.8.2 Pulse Frequency Input

| F809 Max Input Pulse Frequency (Hz) | Setting Range:0～9999 | Mfr Value: 5000 |
| --- | --- | --- |
| F810 Corresponding Frequency for Max Input Pulse Frequency (Hz) | Setting Range: 0.00～F111 | Mfr Value: 50.00 |

● As F204＝7 (P26) and F408=23 (P34), inverter’s running frequency can be controlled through pulse frequency input by OP1 terminal.

● F809 provides the max pulse frequency allowed for inverter’s input. Inverter will not proceed in case of exceeding this frequency.

| F811 Filtering Time Constant (S) | Setting Range: 1.0～10.0 | Mfr Value: 3.0 |
| --- | --- | --- |

● Filter the input analog signal. The bigger the value is, the steadier the analog set frequency is, but will have a slow response.

5.9 Communication Parameters

| F900 485 Communication Interface Function Selection | Setting Range: 0: computer 1:485 Communication Control Enclosure | Mfr Value: 1 |
| --- | --- | --- |

● This function is used for selecting inverter’s communication type:

0: Computer will communicate and control inverter through 485 interface.

1: “Communication Control Enclosure 485” works and controls inverter through 485. It will take 9600 bit (F903＝3) as default communication Baud rate in this control mode, which can not be changed.

| F901 Communication Address | Setting Range: 1～127: inverter address | Mfr Value: 1 |
| --- | --- | --- |

● Set the communication address for inverter. Each address in the same connection n et shall be exclusive and unrepeatable.

| F902 Odd/Even Calibration | Setting Range: 0: no calibration 1:odd calibration 2:even calibration | Mfr Value: 0 |
| --- | --- | --- |

● Select calibration type for RS-485 communication.

● As F900＝1, this function does not work.

| F903 Communication Baud Rate (bit) | Setting Range: 1:2400 2:4800 3:9600 4:19200 | Mfr Value: 3 |
| --- | --- | --- |

● Selecting data transmission ratio between inverter and computer remote control.

● As F900＝1, “Communication Control Enclosure 485” will take 9600bit as default communication Baud rate, which can not be changed.

VI. Simple Mode of Operation

6.2 Speed Control

YTD-G series inverter has multiple ways of speed control like “keypad and terminal digital speed control”, “multi-speed control (including multi-speed running, automatic circulating running, 8-stage speed running, compound speed control”, “analog signal single channel speed control”, “analog signal compound speed control”, “coding speed control”, “jogging speed control” and “computer speed control” and so on. All these must correspond with parameter settings, to be detailed as follows:

1) Keypad, Terminal Digital Speed Control: F204＝0 or 1

Under this setting, inverter adopts the way of keypad, terminal digital speed control, and speed can be adjusted with “▲/▼” keys on the keypad or “UP” and “DOWN” terminals to achieve dynamical speed control. Among which the function of “UP” and “DOWN” terminals speed control is defined by F408～F415 and “UP” terminal equals to “▲” key on the keypad and “DOWN” terminal equals to “▼” key on the keypad.

e.g. as F409=11, OP2 is defined as “UP” terminal that is connected with CM and frequency rises; as F410=12, OP3 is defined as “DOWN” terminal, that is connected with CM and frequency drops.

As F204＝0, no adjusting result is saved after inverter is suddenly turned off;

As F204＝1, adjusting result is saved after inverter is suddenly turned off;

Manufacturer’s default speed-control mode is F204＝0.

Operation control is selected by F200: F200＝0 keypad control/485 communication control, F200＝1 terminal control，F200＝2 computer control.

Operation direction of keypad control is selected by F207: F207＝0 forward, F207＝1 reverse.

Terminal control way is selected by F208: F208＝0 ,two-line type 1; F208＝1 , two-line type 2; F208=2,three-line type 1; F208=3 , three-line type 2, F208＝4 start/stop controlled by direction pulse.

Frequency adjusting step length is set by F230 with setting scope of 0.01～1.00Hz.

Stopping mode is selected by F121: F121＝0 stop by deceleration time, F121＝1 free stop. Free stop is selected by F700: F700＝0 stop at once, F700＝1 delayed stop. F701 sets delayed stop time.

2) Multi-Speed Control: F204＝2

Multi-speed control is further divided into 4 modes: multi-speed running, automatic circulating running, 8-stage speed running and compound stage speed running, which is selected by F210: F210=0 multi-speed running, F210=1 automatic speed running, F210=2 8-stage speed running .

Stage-speed changing control is done by F209: F209＝0 allows no adjustment to segment speeds, F209＝1 allows adjustment to segment speeds. Multi-segment-speed’s related parameters are set by F300～F344.

Operation control is selected by F200: F200＝ 0 keypad control/485communication control, F200＝1 terminal control，F200＝2 computer control .

Terminal control mode is selected by F208: F208＝0 ,two-line type 1; F208＝1 , two-line type 2; F208=2, three-line type 1; F208=3 , three-line type 2, F208＝4 start/stop controlled by direction pulse .

Adjustment step length of frequency is set by F230. Setting range is 0.01～1.00Hz.

Stop mode is selected by F121: F121＝0 stop by deceleration time, F121＝1 free stop. Free stop is selected by F700: F700＝0 stop at once, F700＝1 delayed stop. F701 sets time of delay stop.

a. Multi-Speed Running: F204=2, F210=0

“Multi-speed” involves 7 speeds (their frequency values, acceleration and deceleration time and so on can be revised via parameters) set in the inverter and is operated by defined “multi-speed terminal 1”, “multi-speed terminal 2” and “multi-speed terminal 3”. The status combination that they are connected or disconnected with “CM” can call separately any speed of the “multi-speed”.

e.g., F408=1, F409=2, F410=3, then OP1, OP2, OP3 are separately defined as “multi-speed terminal 1”, “multi-speed terminal 2” and “multi-speed terminal 3”. See Table 6-1 for how to make compound calls:

Table 6-1 Multi-Speed Calling & Corresponding Parameters Setting

| Multi-speed terminal 3 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Multi-speed terminal 2 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 |
| Multi-speed terminal l | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |
| Stage speed Calling | Stop | 1st Speed | 2nd Speed | 3rd Speed | 4th Speed | 5th Speed | 6th Speed | 7th Speed |
| Acceleration time |  | F301 | F307 | F313 | F319 | F325 | F331 | F337 |
| Deceleration time |  | F304 | F310 | F316 | F322 | F328 | F334 | F340 |
| Frequency Set |  | F302 | F308 | F314 | F320 | F326 | F332 | F338 |
| Operation direction | keypad control (F200＝0） |  | F300 | F306 | F312 | F318 | F324 | F330 | F336 |
|  | terminal control (F200＝1) | Realized by the control mode of terminals FWD, REV, and X (F208) |

Note: “1” in the table means the terminal of input signal is connected with CM; “0” means the terminal of input signal is disconnected with CM.

b. Automatic circulating operation: F204=2, F210=1

“Automatic circulating operation” means “multi-segment-speed” automatic circulating operation, i.e.,inverter shall automatically operate as per acceleration/deceleration time, operation time, operation frequency and operation direction set in “each stage speed” as required by users after “operation” command is given; when operation reaches the set time value, inverter shall automatically switch among stage speeds. During the operation, inverter shall continuously operate according to the set parameters if no command of “stop” is given or it doesn’t reach the set value by F212 (operation times of auto circulation).

“Auto circulating operation” can be called by “run” key or the defined “operation” terminal and can be automatically removed by the setting of F212 or by “stop” key on the keypad or the defined “stop” terminal.

“Auto circulating operation” can realize auto circulating operation of 2nd～7th speeds (set by F211). Once the times of circulation is reached (set by F212), inverter shall stop automatically or remain in stable operation at the final stage speed frequency (set by F213).

e.g.: F211＝ 7, select auto circulating operation of “7-stage speed”. F212 ＝1000, automatic circulating operation for 1000 times. F213 ＝ 0, it automatically stops after circulating operation end.

As the YTD-G inverter is carrying the function of “auto-circulating operation”, it shall directly switch from current speed to the next speed (as shown in Fig 6-2) without stopping and waiting if stopping and waiting time equals to zero, i.e., the setting of F305, F311, F317, F323、F329, F355 and F341 is 0.0.

If “ Stop/wait time” is more than 0, i.e., the values of F305, F311, F317, F323, F329, F355 and F341 are set more than 0.0, inverter shall first stop waiting and then switch to the next speed (as shown in Figure 6-3) If the operation direction among stage speeds is different, like F300＝0, F306=1, F312＝0, then the switch process of speeds shall be stop first before switch to the next speed and the switch process shall carry out the death area time of forward and reverse switch (F120—P23), as shown in Fig 6-4.

c. 8th Speed Operation: F204＝2, F210＝2

The 8-stage speed operation consists of 7 speed frequencies and the target frequency F113, which are also operated by the defined “multi-speed terminal 1”, “multi-speed terminal 2”and“multi-speed terminal 3”. The status combination that the 3 terminals are connected or disconnected with “CM” can call separately any of the 8 speeds.

e.g.: F408=1, F409=2 and F410=3, the terminals of OP1, OP2 and OP3 are separately defined as “multi-speed terminal 1” “multi- speed terminal2”and“multi- speed terminal 3”. See Table 6-2 for how to make compound call:

Table 6-2  8-Speed Calling & Its Corresponding Parameter Setting

| Multi-speed terminal 3 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Multi-speed terminal 2 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 |
| Multi-speed terminal l | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 |
| Stage speed Calling | 1st Speed | 2nd Speed | 3rd Speed | 4th Speed | 5th Speed | 6th Speed | 7th Speed | 8th Speed |
| Acceleration time | F114 | F301 | F307 | F313 | F319 | F325 | F331 | F337 |
| Deceleration time | F115 | F304 | F310 | F316 | F322 | F328 | F334 | F340 |
| Frequency Set | F113 | F302 | F308 | F314 | F320 | F326 | F332 | F338 |
| Operation direction | keypad control (F200＝0） | F207 | F300 | F306 | F312 | F318 | F324 | F330 | F336 |
|  | terminal control (F200＝1) | Realized by the control mode of terminals FWD, REV, and X (F208) |

Note: “1” in the table means input signal terminal is connected of with CM; whereas “0” means disconnection of input signal terminal from CM.

d. Compound on speed control: F204＝2, F210＝0 or 2, F342＝1

Compound speed control means the speed control mode controlled jointly by multi-speed control, digital speed control and analog speed control. This speed control mode is only effective to multi-speed and 8-stage speed running but is not valid to auto circulating operation.

When jointly controlled by multi-speed control and digital speed control (F343＝0), the running frequency of each speed will be the total of multi-speed setting frequency and the setting value of digital frequency. The setting value of digital frequency is set by F344 with a range of 0.00～20.00Hz.

When jointly controlled by multi-speed control and analog speed control(F343＝1), the operation frequency of each speed is the total values set by multi-speed frequency and I2 channel analog signal whose value is set at the range of 0～10V ( provided through I2 channel by peripheral equipment) corresponding with a range of 0～12Hz.

Stage-speed changing control is selected by F209: F209＝0 not allowed to changing to stage speed; F209＝1 allowed to changing to stage speed.

The related parameter of multi-speed is set by F300～F344.

Operation control is selected by F200: F200＝0 keypad control/485communication control; F200＝1 terminal control; F200＝2 computer remote control .

Operation direction of keypad control is selected by F207: F207＝0 forward, F207＝1 reverse .

Terminal control mode is selected by F208: F208＝0 ,two-line type 1; F208＝1 , two-line type 2; F208=2, three-line type 1; F208=3 , three-line type 2, F208＝4 start/stop controlled by direction pulse .

The adjustment step length of frequency is set by F230 with the range of 0.01～1.00Hz .

Stop mode is selected by F121: F121=0 stop by deceleration time, F121=1 free stop, which is chosen by F700: F700=0 stop immediately, F700＝1 delayed stop. F701 sets delay stop.

3) Single channel analog signal speed control: F204=3, 4 or 10 Note3

Analog speed control means to adjust inverter’s output frequency by the analog signal of voltage (or current), during which, voltage analog signal can be defined by the external potentiometer or that of the keypad control unit, or it can also be defined by output analog signal of other facilities. Current analog signal can be defined by corresponding sensors or by output of other control facilities.

As F204=3, The speed control signal of analog signal shall be input by terminal “V2”; as F204=4, speed control signal of analog signal shall be input by terminal “I2”; F204＝10 is used to select the control speed of the analog signal of keypad potentiometer (Vk) Note 3.

Different ways of speed control can be reached by using jumper terminals and function parameter settings together (see details on for Application of Jumper Terminals.)

Related parameters of analog signal are set by F800～F811 .

Operation control is selected by F200: F200＝0 keypad control/485 communication control, F200＝1 terminal control, F200＝2 computer remote control .

Operation direction of keypad control is selected by F207: F207＝0 forward，F207＝1 reverse .

Terminal control mode is selected by F208: F208＝0 ,two-line type 1; F208＝1 , two-line type 2; F208=2, three-line type 1; F208=3 , three-line type 2, F208＝4 start/stop controlled by direction pulse .

Stop mode is selected by F121: F121＝0 stop by deceleration time, F121＝1 free stop. Of which free stop mode is selected by F700: F700＝0 immediate stop, F700＝1 delayed stop. Time of delayed stop is set by F701 .

4) Compound Speed Control of Analog signal: F204＝5, 6 or 9

For compound speed setting, analog signal is input through terminals of “V2” and “I2”. For F204=5, the result of compound speed control is k1×V2＋k2×I2; as F204=6, the result of compound speed control is k1×V2-k2×I2; as F204=9, the result of compound speed control is k1×V2＋k2×(I2-5V). The “V2” and “I2” in the formula mean the analog signal input through channels V2 and I2.

For compound speed control, there is a function with the programmable input terminal (OP1～OP8), which may be used to switch the controls of dual-way analog signal and single-way analog signal. For single-way analog signal control, V2 channel control is considered valid by default. For instance F409＝20: when OP2 is disconnected from CM, it is dual-way analog signal control; when OP2 is connected with CM, V2channel control works, equal to F204＝3.

Different speed control mode may be realized by using jumper terminals and function parameter settings together (refer to Application of Jumper Terminal on for details)

Ratio coefficients k1 and k2 are set by F214 and F215 functional code .

Related parameters of analog signal is set by F800～F811 .

Operation control is selected by F200: F200＝ 0 keypad control/485communication control, F200＝1 terminal control, F200＝2 computer remote control .

Operation direction of keypad control is selected by F207: F207＝0 forward，F207＝1 reverse .

Terminal control mode is selected by F208: F208＝0 ,two-line type 1; F208＝1 , two-line type 2; F208=2, three-line type 1; F208=3 , three-line type 2, F208＝4 start/stop controlled by direction pulse .

Stop mode is selected by F121: F121＝0 stop as deceleration time, F121＝1 free stop. Of which, free stop mode is selected by F700: F700＝0 immediate stop, F700＝1 delayed stop. F701 sets time of delayed stop.

5) Coding Speed Control: F204=8

Set the input terminal (OP1～OP8) as the coding speed control function. The different switch status combinations for terminal mean the 8-binary data. OP8 is the highest bit. and OP1 is the lowest bit. It is further stipulated that connection between terminal and “CM” is binary 1 and disconnecting with “CM” is binary ‘0”.

Through inverter, the 8-binary data input by OP1～OP8 shall be changed to decimal system value, the ratio with value 255 will then multiply with inverter’s max frequency and get the actual output frequency of coding speed control.

e.g.: if max frequency F111＝50.00Hz, F415=18 and OP8 terminal connects with CM terminal, then input binary data 10000000, which is 128 in decimal. The operation frequency will therefore be (128／255)×50＝25.10Hz.

6) Jogging Speed Control: F200＝1

In mode of terminal control (F200＝1), when function of certain programmable input terminal (OP1～OP8) is defined as jogging function, jogging speed control can be reached by short connection of the terminal with CM.

The jogging frequency is set by F124 with range: F112 ( min frequency)～F111( max frequency).

The jogging acceleration /deceleration time is set by F125 and F126, with range of 0.1～3000S.

The direction of jogging operation is included in the definition for terminal function: 9 is forward running and 10 is reverse running.

Stop mode is selected by F121: F121＝0 stop as deceleration time, F121＝1free stop. Of which, free stop is selected by F700: F700＝0 instant stop, F700＝1 delayed stop. F701 sets delayed stop time.

7）Computerized Speed Control: F900＝0

Computerized speed control means that computer will communicate via 485 to control the operation of inverter.

The communication address is selected by F901 with setting range of 1～127. It should be noted that computer’s “broadcasting address” is 255. When implementing the broadcasting command, computer may control all inverters in the network with no need for inverters to set broadcasting address.

Communication checking type is selected by F902: F902＝0 non- checking, F902=1 odd checking, F902＝2 even checking.

Communication Baud rate is set by F903: 2400bit for F903＝1, 4800bit for F903＝2, 9600bit for F903＝3, and 19200bit for F903＝4.

Stop mode is selected by F121: F121＝0 stop by deceleration time, F121＝1 free stop. Of which, free stop is selected by F700: F700＝0 instant stop, F700＝1 delayed stop. F701 sets delayed stop time.

Appendix 1        Trouble Shooting

When malfunction occurs to inverter or motor, users may get the type of malfunction, the bus voltage, output current and frequency of the moment that malfunction occurs through reading F720～F725, and carry out inspection and analysis according to the following table or contact manufacturer when necessary.

Table 1   Malfunctions & Solutions

| Malfunction Display | Description | Causes | Solutions |
| --- | --- | --- | --- |
| OC1 | Acceleration over-current | Acceleration time too short | Prolong acceleration time |
|  |  | Short circuit on the side of output | Motor cable damaged or not; Motor insulation level is satisfactory to requirement or not |
|  |  | Inverter’s power is small | Select bigger power inverter |
|  |  | Improper selection of V/F curve | Adjust V/F curve as per actual load; Reduce V/F compensation value |
|  |  | Restart the motor in rotation | Restart when motor completely stops. |
|  |  | Overloaded | Reduce load |
| OC2 | Deceleration over-current | Too short for deceleration time | Extend deceleration time |
|  |  | high load inertia | Add proper energy consumption braking parts |
| OC3 | Constant overcurrent | Short circuit on the side of output | Check if motor cable is damaged |
|  |  | Sudden change of loading | Reduce sudden change of loading |
|  |  | Abnormal loading | Check the loading |
| OE1 | Acceleration overvoltage | higher input voltage | Check if the input voltage is normal |
| OE2 | Deceleration overvoltage | Too short time for deceleration (compared to the capacity of regeneration) | Extend deceleration time |
|  |  | high load inertia | Add proper energy consumption braking part |

Table 1 continued

| Malfunction Display | Description | Causes | Solutions |
| --- | --- | --- | --- |
| OE3 | Over voltage of constant speed | Abnormal change of input voltage | Check input voltage or add reactor |
|  |  | Big loading inertia | To add proper energy consumption braking parts |
| AdEr | Galvanoscopy malfunction | The wire or inserting parts between control PCB and power PCB gets loose | Check and reconnection |
|  |  | Galvanoscopy elements damaged | Seek manufacturers’ service |
| OL1 | Inverter overloading | Too much overload | Reduce load |
|  |  | Acceleration time too short | Extend acceleration time |
|  |  | Improper V/F curves | Adjust the V/F curve, and properly lower compensation value |
|  |  | Too much DC braking | Reduce DC braking current, extend braking time |
|  |  | Inverter power small | Select inverter with bigger power |
| OL2 | Motor overload | Improper V/F curve | Adjust the V/F curve, and properly lower compensation value |
|  |  | General motor runs at low speed with big load for long time | Special motor is needed for long time low speed running |
|  |  | Rotation of motor is jammed or loading suddenly gets bigger. | Reduce loading or the sudden change of loading |
|  |  | Incorrect setting for motor overloading protection coefficient | Correctly set the protection coefficient for motor overloading |
| PEr | Out-phase protection | Out-phase with 3- phase power input | Check if power input is normal; Check the wiring is correct |
|  |  | Serious imbalance with 3-phase input power | Check if power input is normal |
|  |  | Power off unexpectedly with inverter’s input power | Normal indication |
| LU | Undervoltage protection | slightly low with input voltage | Check if voltage is correct |
|  |  | Power off unexpectedly with inverter input power | Normal indication |

Table 1 continued

| Malfunction Display | Description | Causes | Solutions |
| --- | --- | --- | --- |
| ESP | External emergency stop | Press “stop/reset” key not in mode of keypad control (F200≠0) | Correctly set the functional parameters for F201& F200 |
|  |  | “External Emergency stop” terminal closes | Disconnect malfunction terminal after removal of external malfunction; Change the function of “programmable input terminal” |
|  |  | Press “stop/reset” in case of stalling | Normal indication |
| ErP | Peripheral equipment malfunction | Terminal of “Peripheral equipment malfunction” closes | Disconnect malfunction terminal after removal of external malfunction; Change the function of “programmable input terminal” |
| Err | Serious external interference | Strong electromagnetic interference with inverter’s surroundings | Check if the surroundings are satisfactory for use of inverter as required in 3.1.2 |
| OH | Over temperature | Too high surrounding temperature | Reduce surrounding temperature |
|  |  | Fan damaged | Change the fan |
|  |  | Installation position is not fit for ventilation | Install as per manual and improved ventilation |
|  |  | Radiators too dirty | Clean the inlet and outlet and the radiators |
|  |  | Power module is abnormal | Seek manufacturers’ service |
| Cb | Contactor does not suck | Too low voltage of power network | Check the voltage |
|  |  | Contactor damaged | Change the main-loop contactor |
|  |  | Trouble with the control loop | Seek manufacturers’ service |

Table 1 continued

| Malfunction Display | Description | Causes | Solutions |
| --- | --- | --- | --- |
| －E.r－ | Communication malfunction | Baud rate setting is incorrect when communicating with 485 communication control enclosure | Change inverter’s Baud rate to manufacturer’s value |
|  |  | Incorrect communication address setting | Unify inverter address with 485 communication control enclosure |
|  |  | Malfunction occur with communication circuits | Seek manufacturers’ service |
| Motor doesn’t work | Abnormal power-network voltage | Check if power-network voltage is normal |
|  | Wrong wiring | Check the wiri ng |
|  | Overloading | Reduce loading |
| Power tripping | Short circuits on input side | Check the input wiring |
|  | Too small capacity of air switch | Increase air switch capacity |
|  | Overloading | Reduce loading |
| Motor works but unable to control speed | Error setting for related parameters | Correctly set related parameters as to parameter description |
|  | Serious overloading | Reduce loading |
| Instable rotation of motor | Sudden increase of overloading | Reduce the change of loading |
|  | Power of inverter is slightly small | Select inverter of bigger power |
|  | Serious electromagnetic interference | Check if surroundings is satisfactory for use of inverter as required in 3.1.2 |

Appendix 2     Function Code Zoom Table

| Class | Function Code | Definition | Setting Range | Mfr Value | Note |
| --- | --- | --- | --- | --- | --- |
| Basic Parameters | F100 | User’s Code | 0～9999 | 8 | √ |
|  | F101 | Reserved |  |  |  |
|  | F102 | Inverter’s Rated Current (A) |  | Subject to inverter model | △ |
|  | F103 | Inverter Power (KW) | 0.20～110.0 | Power value of this inverter | △ |
|  | F104 | Reserved |  |  |  |
|  | F105 | Software Edition No. |  | Subject to software edition | △ |
|  | F106 | Inverter’s Input Voltage Type | 1:single phase 3:three phase | Subject to inverter model | △ |
|  | F107 | Inverter’s Rated Input Voltage (V) | 220 or 380 | Subject to inverter model | △ |
|  | F108 | Reserved |  |  |  |
|  | F111 | Max Frequency (Hz) | F112～400.0 | 60.00 | × |
|  | F112 | Min Frequency (Hz) | 0.00～MIN（50.00，F111） | 0.00 | × |
|  | F113 | Digital Setting Frequency (Hz) | F112～F111 | 50.00 | √ |
|  | F114 | 1st Acceleration Time (S) | 0.1～3000 | 20.0 | √ |
|  | F115 | 1st Deceleration Time (S) | 0.1～3000 | 20.0 | √ |
|  | F116 | 2nd Acceleration Time (S) | 0.1～3000 | 20.0 | √ |
|  | F117 | 2nd Deceleration Time (S) | 0.1～3000 | 20.0 | √ |
|  | F118 | Turnover Frequency（Hz） | 50.00～400.0 | 50.00 | × |
|  | F119 | Latent Frequency（Hz） | F112～F111 | 5.00 | √ |
|  | F120 | Forward/Reverse Switchover Dead-Time (S) | 0.0～3000 | 2.0 | √ |
|  | F121 | Stopping Mode | 0: stop by deceleration time 1: free-stop | 0 | × |
|  | F122 | Reverse Running Forbidden | 0: null 1:valid | 0 | × |
|  | F123 | Reserved |  |  |  |
|  | F124 | Jogging Frequency (Hz) | F112～F111 | 5.00 | √ |
|  | F125 | Jogging Acceleration Time (S) | 0.1～3000 | 20.0 | √ |
|  | F126 | Jogging Deceleration Time (S) | 0.1～3000 | 20.0 | √ |
|  | F127 | Skip Frequency A (Hz) | 0.00～F111 | 0.00 | × |
|  | F128 | Skip Width A（Hz） | 0.00～5.00 | 0.00 | × |
|  | F129 | Skip Frequency B (Hz) | 0.00～F111 | 0.00 | × |
| Class | Function Code | Definition | Setting Range | Mfr Value | Note |
| Basic Parameters | F130 | Skip Width B (Hz) | 0.00～5.00 | 0.00 | × |
|  | F131 | Displays | 1～127 1: Frequency 2:Rotate Speed 4:Count Value 8:Output Current 16:Function-Code Editing 32: Output Voltage 64:Linear Velocity 127: Display All | 127 | √ |
|  | F132 | Number of motor pole pairs | 1～6 | 2 | × |
|  | F133 | Driven system’s drive ratio | 0.1～100.0 | 1.0 | × |
|  | F134 | Transmission-wheel radius (m) | 0.001～1.000 | 0.001 | × |
|  | F135～F138 | Reserved |  |  |  |
|  | F139 | Whether to start automatically after reconnection to power or malfunction | 0:null 1:valid | 0 | × |
|  | F140～F159 | Reserved |  |  |  |
|  | F160 | Reverting to manufacturer values | 0:Not reverting to manufacturer values 1:Reverting to manufacturer values | 0 | × |
| Running control parameters | F200 | Operation Control | 0:Keypad Control/485 Communication Control 1: Terminal Control 2: ComputerRemote Control | 0 | × |
|  | F201 | Key Functions | 0: valid only in mode of keypad control 1: valid in any modes 2: valid at time of keypad 3-line control, controlling start/stop by direction pulse and computer remote control | 0 | × |
|  | F202、F203 | Reserved |  |  |  |
|  | F204 | Basic Speed Control Modes | 0: Setting digital frequency, setting keypad and terminal UP & DOWN, not saving result when power off 1: Setting digital frequency, setting keypad and terminal UP & DOWN, saving result when power off 2: Multi-speed control 3:Analog channel 1 (V2) speed control 4:Analog channel 2(I2) speed control 5:Analog Channel Compound speed-control 1:K1*V2+K2*I2 6:Analog Channel Compound speed-control2:K1*V2－K2*I2 7:Speed control set by pulse frequency 8:Code speed control 9:Analog Channel Compound speed-control3:K1*V2+K2*(I2-5V) 10:Keypad potentiometer speed –control selection Note3 | 0 | × |
| Class | Function Code | Definition | Setting Range | Mfr Value | Note |
| Running control parameters | F205, F206 | Reserved |  |  |  |
|  | F207 | Keypad Direction Set | 0: Forward 1: Reverse | 0 | √ |
|  | F208 | Terminal control mode | 0: two-line type 1 1: two-line type 2 2: three-line type 1 3: three-line type 2 4:Start/stop controlled by direction pulse | 0 | × |
|  | F209 | Stage-speed-Changing | 0:Adjustment stage-speed forbidden 1:Adjusting stage-speed allowed | 0 | × |
|  | F210 | Stage-Speed Types | 0: Multi-stage speed running 1: Auto circulation running 2: 8th-stage speed running | 0 | × |
|  | F211 | Auto Circulation Running Speed Selection | 2～7 | 7 | × |
|  | F212 | Auto Circulation Running Times Selection | 0～9999 | 0 | √ |
|  | F213 | Free Running Selection after Auto Circulation Running | 0: Stop 1: Keep running at last stage speed | 0 | √ |
|  | F214 | k1 | 0.0～10.0 | 1.0 | √ |
|  | F215 | k2 | 0.0～10.0 | 1.0 | √ |
|  | F216～F220 | Reserved |  |  |  |
|  | F221 | Count Frequency Divisions | 1～1000 | 1 | × |
|  | F222 | Set Count Times | F224～9999 | 1 | × |
|  | F223 | Reserved |  |  |  |
|  | F224 | Designated Count Times | 1～F222 | 1 | × |
|  | F225～F229 | Reserved |  |  |  |
|  | F230 | Frequency setting Step Length (Hz) | 0.01～1.00 | 0.01 | × |
|  | F231～F260 | Reserved |  |  |  |
| Multi-Speed Parameters | F300 | 1st stage-Speed Running Direction | 0: Forward 1: Reverse | 0 | √ |
|  | F301 | 1st stage-Speed Acceleration Time | 0.1～3000 | 20.0 | √ |
|  | F302 | 1st stage-Speed Running Frequency | F112～F111 | 5.00 | √ |
|  | F303 | 1st stage-Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F304 | 1st stage-Speed Deceleration Time | 0.1～3000 | 20.0 | √ |
|  | F305 | 1st stage-Speed Stop/Waiting Time | 0.0～3000 | 0.0 | √ |
| Class | Function Code | Definition | Setting Range | Mfr Value | Note |
| Multi-Speed Parameters | F306 | 2nd stage-Speed Running Direction | 0: Forward 1: Reverse | 1 | √ |
|  | F307 | 2nd stage-Speed Acceleration Time | 0.1～3000 | 20.0 | √ |
|  | F308 | 2nd stage-Speed Running Frequency | F112～F111 | 10.00 | √ |
|  | F309 | 2nd stage-Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F310 | 2nd stage-Speed Deceleration Time | 0.1～3000 | 20.0 | √ |
|  | F311 | 2ndstage-Speed Stop/Waiting Time | 0.0～3000 | 0.0 | √ |
|  | F312 | 3rd stage-Speed Running Direction | 0: Forward 1: Reverse | 0 | √ |
|  | F313 | 3rd stage-Speed Acceleration Time | 0.1～3000 | 20.0 | √ |
|  | F314 | 3rd stage-Speed Running Frequency | F112～F111 | 15.00 | √ |
|  | F315 | 3rd stage-Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F316 | 3rd stage-Speed Deceleration Time | 0.1～3000 | 20.0 | √ |
|  | F317 | 3rd stage-Speed Stop/Waiting Time | 0.0～3000 | 0.0 | √ |
|  | F318 | 4th stage-Speed Running Direction | 0: Forward 1: Reverse | 1 | √ |
|  | F319 | 4th stage-Speed Acceleration Time | 0.1～3000 | 20.0 | √ |
|  | F320 | 4th stage-Speed Running Frequency | F112～F111 | 20.00 | √ |
|  | F321 | 4th stage-Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F322 | 4th stage-Speed Deceleration Time | 0.1～3000 | 20.0 | √ |
|  | F323 | 4th stage-Speed Stop/Waiting Time | 0.0～3000 | 0.0 | √ |
|  | F324 | 5th stage-Speed Running Direction | 0: Forward 1: Reverse | 0 | √ |
|  | F325 | 5th stage-Speed Acceleration Time | 0.1～3000 | 20.0 | √ |
|  | F326 | 5th stage-Speed Running Frequency | F112～F111 | 25.00 | √ |
|  | F327 | 5th stage-Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F328 | 5th stage-Speed Deceleration Time | 0.1～3000 | 20.0 | √ |
|  | F329 | 5th stage-Speed Stop/Waiting Time | 0.0～3000 | 0.0 | √ |
|  | F330 | 6th stage-Speed Running Direction | 0: Forward 1: Reverse | 0 | √ |
|  | F331 | 6th stage-Speed Acceleration Time | 0.1～3000 | 20.0 | √ |
|  | F332 | 6th stage-Speed Running Frequency | F112～F111 | 30.00 | √ |
|  | F333 | 6th stage-Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F334 | 6th stage-Speed Deceleration Time | 0.1～3000 | 20.0 | √ |
|  | F335 | 6th stage-Speed Stop/Waiting Time | 0.0～3000 | 0.0 | √ |
|  | F336 | 7th stage-Speed Running Direction | 0: Forward 1: Reverse | 0 | √ |
|  | F337 | 7th stage-Speed Acceleration Time | 0.1～3000 | 20.0 | √ |
| Class | Function Code | Definition | Setting Range | Mfr Value | Note |
| Multi-Speed Parameters | F338 | 7th stage-Speed Running Frequency | F112～F111 | 35.00 | √ |
|  | F339 | 7th stage-Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F340 | 7th stage-Speed Deceleration Time | 0.1～3000 | 20.0 | √ |
|  | F341 | 7th stage-Speed Stop/Waiting Time | 0.0～3000 | 0.0 | √ |
|  | F342 | Selection of compound speed control for stage-speeds | 0: Not Allowed 1:Allowed | 0 | √ |
|  | F343 | Selection of compound speed control mode for stage-speeds | 0:Multi-stage Speed Running Frequency + Value set for F344 1: Multi-stage speed Running Frequency + I2 Channel Analog Values | 0 | √ |
|  | F344 | Digital Frequency Setting For Compound Speed Control(Hz) | 0.00～20.00 | 0.00 | √ |
|  | F345～F360 | Reserved |  |  |  |
| Programmable Input/Output Teminal Parameters | F400～F407 | Reserved |  |  |  |
|  | F408 | OP1 Terminal Function Definition | 0: No function 1: Multi-speed terminal 1 2: Multi-speed terminal 2 3: Multi-speed terminal 3 4: Reset 5: Free stop 6: Reserved 7: External Emergency Stop 8: Acceleration / Deceleration Prohibited 9: Jogging Forward Running JOGF 10: Jogging Reverse Running JOGR 11:Frequency increasing by degrees UP 12:Frequency decreasing by degrees DOWN 13: “FWD” Terminal 14: “REV” Terminal 15:Three-Line type Input Teminal of “Ｘ” 16:Switchover of Acceleration /Deceleration time 17:Peripheral equipment Malfunction 18:Coding speed control input 19: Close loop switched to open loop 20: Compound channel speed control switch to single channel speed control 21: Teminal Counting 22: Count Value Reset to Zero 23: Pulse Frequency Input terminal (only valid for OP1) | 9 | × |
|  | F409 | OP2 Terminal Function Definition |  | 1 | × |
|  | F410 | OP3 Terminal Function Definition |  | 2 | × |
|  | F411 | OP4 Terminal Function Definition |  | 3 | × |
|  | F412 | OP5 Terminal Function Definition |  | 7 | × |
|  | F413 | OP6 Terminal Function Definition |  | 13 | × |
|  | F414 | OP7 Terminal Function Definition |  | 14 | × |
|  | F415 | OP8 Terminal Function Definition |  | 4 | × |
| Class | Function Code | Definition | Setting Range | Mfr Value | Note |
| Programmable Input/Output Teminal Parameters | F416 | Relay Output | 0: No function 1: Inverter malfunction protection 2: Over latent frequency 3: Free stop 4: Inverter in operation 5: During DC braking 6: Indicating switchover of Acceleration/Deceleration 7: Reaching the set count value 8:Reaching designated count value 9: Overload early warning signal 11: Indication function when reaching a certain frequency 10: Reserved 12: Reserved 13: Reserved | 1 | × |
|  | F417 | OUT Terminal Output |  | 4 | × |
|  | F418 | FM Output Function Selection | 0: Indicate output frequency value 1: Indicate output current value | 0 | √ |
|  | F419 | FM Output Calibration (％) | 0～200 | 100 | √ |
|  | F420 | IM (FM) Output Range Selection | 0:0～20mA（0～10V） 1:4～20mA（2～10V） | 0 | √ |
|  | F422 | Indication function when reaching a certain frequency | Max(5.00,F112)~F111 | 5.00 |  |
| V/F Control Parameters | F500 | Slip Compensation | 0.00～0.08 | 0.03 | × |
|  | F501 | V/F Curve Control Mode | 0:Beeline 1:Polygonal line 2:Square | 0 | × |
|  | F502 | Torque Promotion（％） | 1～MIN（15，F506） | 5 | × |
|  | F503、F504 | Reserved |  |  |  |
|  | F505 | User-Defined Frequency Point１(Hz) | F112～F507 | 10.00 | × |
|  | F506 | User-Defined Voltage Point１(％) | F502～MIN(100，F508) | 30 | × |
|  | F507 | User-Defined Frequency Point 2(Hz) | F505～F118 | 20.00 | × |
|  | F508 | User-Defined Voltage Point 2 (％) | F506～MIN(100，F509) | 40 | × |
|  | F509 | Voltage Corresponding of Turnover Frequency (％) | F508～100 | 100 | × |
|  | F510 | Reserved |  |  |  |
|  | F511 | Auto Voltage Adjusting | 0: No adjusting 1:Adj usting | 0 | × |
|  | F512 | Carrier-Wave Frequency Setting (kHz) | 1～values set as per inverter model | Subject to inverter’s setting value | × |
| Class | Function Code | Definition | Setting Range | Mfr Value | Note |
| V/F Control Parameters | F513 | Randum Carrier-Wave Selection | 0: Not allowed 1:Allowed | 1 | × |
|  | F514 | DC Braking Function Selection | 0: Not allowed 1: Braking during start 2: Braking during stop 3: Braking for Start＋stop | 0 | × |
|  | F515 | Initial Frequency of DC Braking (Hz) | 0.00～5.00 | 5.00 | √ |
|  | F516 | DC Braking Current (％) | 0～150 | 100 | √ |
|  | F517 | Braking Lasting Time During Starting (S) | 0.0～10.0 | 5.0 | √ |
|  | F518 | Braking Lasting Time During Stopping (S) | 0.0～10.0 | 5.0 | √ |
|  | F519 | Energy Consumption Brake Ratio (％) | 0～100 | 50 | × |
|  | F520～F524 | Reserved |  |  |  |
|  | F525 | Stalling Adjusting Function Selection | 0: Not allowed 1:Allowed | 0 | × |
|  | F526 | Stalling Current Adjusting (％) | 120～200 | 160 | × |
|  | F527 | Stalling Voltage Adjusting (％) | 120～200 | 140 | × |
|  | F528～F560 | Reserved |  |  |  |
| PI AdjustingParameters | F600 | PI Adjusting Function Selection | 0: Not allowed 1:Allowed | 0 | × |
|  | F601 | PI Adjusting Channel Selection | 0: Digital setting 1: V2 channel setting 2: I2 channel setting | 0 | × |
|  | F602 | PI Adjustment Dig it Provided (V) | 0.00～10.00 | 5.00 | × |
|  | F603 | PI Adjusting Feedback Channel Selection | 0: V2 channel feedback 1: I2 channel feedback 2: OP1 pulse channel feedback | 0 | × |
|  | F604 | Min Analog Set by PI (V) | 0.00～F606 | 0.00 | × |
|  | F605 | Corresponding Feedback for Min Analog Set by PI (V) | 0.00～10.00 | 0.00 | × |
|  | F606 | Max Analog Set by PI (V) | F604～10.00 | 10.00 | × |
|  | F607 | Corresponding Feedback for Max Analog Set by PI (V) | 0.00～10.00 | 10.00 | × |
|  | F608 | Proportion Gain | 1～1000 | 100 | √ |
|  | F609 | Integration Time (S) | 0.1～10.0 | 0.1 | √ |
|  | F610 | Sampling Cycle (S) | 0.1～10.0 | 0.1 | √ |
| Class | Function Code | Definition | Setting Range | Mfr Value | Note |
| PI Adjusting Parameters | F611 | PI Adjusting Accuracy (％) | 0～20 | 5 | √ |
|  | F612 | PI Adjusting Polarity | 0:Negative feedback adjusting 1:Positive feedback adjusting | 0 | × |
|  | F613～F660 | Reserved |  |  |  |
| Timing Control & Definable Protection Parameters | F700 | Mode selection for Free -Stop | 0: Immediate stop 1: stop delay | 0 | × |
|  | F701 | Delay time of Free-Stop and Programmable Output Terminal’s Action (S) | 0.0～60.0 | 0.0 | × |
|  | F702 | Fan Control Selection (valid only for 18.5～110KW inverter) | 0: Temperature controlled fan running 1: Not temperature controlled fan running | 0 | × |
|  | F703～F704 | Reserved |  |  |  |
|  | F705 | Allowed Auto-Start times | 0～5 | 3 | × |
|  | F706 | Interval time of Auto-restart (S) | 0.0～10.0 | 3.0 | × |
|  | F707、F708 | Reserved |  |  |  |
|  | F709 | Under-voltage Protection Value (V) | 200～420 | Subject to inverter’s model | △ |
|  | F710～F714 | Reserved |  |  |  |
|  | F715 | Overload Adjusting Gains | 0～1000 | Adjusting value | ○ |
|  | F716 | Inverter Overloading Coefficient (％) | 150～180 | Adjusting value | ○ |
|  | F717 | Motor Overloading Coefficient (％) | 20～120 | Adjusting value | ○ |
|  | F718、F719 | Reserved |  |  |  |
|  | F720 | Third Malfunction Type by Counting DOWN | 0: No Trouble 1: Acceleration over-current 2: Deceleration over-current 3: Constant-speed over-current 4: Acceleration over-voltage 5: Deceleration over-voltage 6: Constant-speed over-voltage 7: Undervoltage 9: Inverter overload 10: Motor overload 11: Excess temperature 12:User’s password error/serious exterior interference 13: Out-phase 15: Emergency stop 19:Galvanoscopy error 21:Peripheral equipment Malfunction |  | △ |
|  | F721 | Second Malfunction Type by Counting DOWN |  |  |  |
|  | F722 | Latest Malfunction type |  |  |  |
| Class | Function Code | Definition | Setting Range | Mfr Value | Note |
| Timing Control & Definable Protection Parameters | F723 | The Last Malfunction Frequency (Hz) |  |  | △ |
|  | F724 | The Last Malfunction Current (A) |  |  | △ |
|  | F725 | The Last Malfunction Voltage (V) |  |  | △ |
|  | F726～F760 | Re served |  |  |  |
| Analog Parameters | F800 | Min Analog Input (V) | 0.00～MIN(F801,10.00) | 0.00 | √ |
|  | F801 | Max Analog Input (V) | MAX（0.00，F800）～10.00 | 10.00 | √ |
|  | F802～F806 | Reserved |  |  |  |
|  | F807 | Corresponding Frequency for Min Analog (Hz) | F112～F111 | 0.00 | √ |
|  | F808 | Corresponding Frequency for Max Analog (Hz) | F112～F111 | 50.00 | √ |
|  | F809 | Max Input Pulse Frequency (Hz) | 0～9999 | 5000 | × |
|  | F810 | Corresponding Frequency for Max Input Pulse Frequency (Hz) | 0.00～F111 | 50.00 | × |
|  | F811 | Filtering Time Constant (S) | 1.0～10.0 | 3.0 | √ |
|  | F812～F860 | Reserved |  |  |  |
| Communication Parameters | F900 | 485 Communication Interface Function Selection | 0: Computer 1:485 communication control enclosure | 1 | × |
|  | F901 | Communication Address | 1～127: Inverter address | 1 | × |
|  | F902 | Odd/even calibration | 0: No calibration 1: Odd calibration 2: Even calibration | 0 | × |
|  | F903 | Communication Baud rate (bit) | 1: 2400 2: 4800 3: 9600 4: 19200 | 3 | × |
|  | F904 | No Parameter Mode(valid for Computer Remote Control) | 0::run with parameters 1:run without parameters | 1 | × |
|  | F905~F960 | Reserved |  |  |  |

Remarks: × means that this function code can only be modified at stop.

√ means that this function code can be modified at stop or during running.

△ means that this function code can only be checked but cannot be modified at stop or during running.

○ means that this function code cannot be initialized when inverter’s manufacturer value is restored and can only be modified manually.

Appendix 3    Selection of Braking Resistor & Braking unit

Built-in braking units are available with some of YTD-G series inverters . Power terminals of these inverters include terminals “P” and “B”. They can then be connected with braking resistors externally. Matching standards for the braking resistors are shown in Table 2 below.

Table 2        Selection of Braking Resistance

| Inverter Models | Applicable Motor Power（KW） | Applicable Braking Resistance |
| --- | --- | --- |
| YTD2.2G4T1B | 2.2 | Al Housing 150W/150Ω |
| YTD3.7G4T1B | 3.7 |  |
| YTD4G4T1B | 4 | Al Housing 250W/120Ω |
| YTD5.5G4T1C | 5.5 | Al Housing 250W/120Ω |
| YTD7.5G4T1C | 7.5 | Al Housing 1KW/90Ω |
| YTD11G4T1C | 11 | Al Housing 1.5KW/80Ω |
| YTD15G4T1C | 15 | Al Housing 2KW/60Ω |

Built-in braking units are not available with inverters above three-phase 18.5KW. Power terminals of these inverters include terminals “P” and “B”. They need to be connected with braking resistors externally. Terminals “P” ( or “+”) and “N” (or “－”) of braking unit are connected with inverter’s terminals “P”and “N”. Terminals “P” and “B” of braking unit are connected with braking resistor. Matching standards are shown in Table 3 below.

Table 3             Selection of Braking unit

| Inverter Models | Applicable Motor Power（KW） | Applicable Braking unit Models | Applicable Resistance for Braking unit |
| --- | --- | --- | --- |
| YTD18.5G4T1C | 18.5 | YT-BU-1 | 3KW /45Ω |
| YTD22G4T1C | 22 |  |  |
| YTD30G4T1C | 30 | YT-BU-2 | 4KW /30Ω |
| YTD37G4T1C | 37 | YT-BU-3 | 3KW /45Ω×2（并联） |
| YTD45G4T1C | 45 |  |  |
| YTD55G4T1C | 55 | YT-BU-4 | 6KW /20Ω |
| YTD75G4T1C | 75 | YT-BU-5 | 4KW /30Ω×2（并联） |
| YTD90G4T1C | 90 |  |  |
| YTD110G4T1C | 110 | YT-BU-5 | 6KW /20Ω×2（并联） |
| YTD132G4T1C | 132 | YT-BU-6 |  |
| YTD160G4T1C | 160 | YT-BU-6 |  |
| YTD185G4T1C | 185 | YT-BU-7 |  |
| YTD200G4T1C | 200 | YT-BU-7 |  |
| YTD220G4T1C | 220 | YT-BU-8 |  |
| YTD250G4T1C | 250 | YT-BU-8 |  |
| YTD280G4T1C | 280 | YT-BU-9 |  |
| YTD315G4T1C | 315 | YT-BU-9 |  |
| YTD400G4T1C | 400 | YT-BU-10 |  |

Add:8F Rongxing Building,NO.1851,North Sichuan Road,Shanghai,China

Tel:86-21-51053128  51053127  51054125

Fax:86-21-51053123  51053913

Post Code:200081

E-mail:ytbpq@yatai.sh.cn

http://www.yatai.sh.cn

# Text boxes

Structure Mode Code

B：Plastic Housing

C：Metal Hanging Type

D：Metal Cabinet Type

Software Version Number

Input Voltage Type（2S：Single-phase220VAC，2T：Three-phase220VAC, 4T：Three-phase380VAC）

General Type

Matched Motor Power(2.2KW)

Product Series

YTD  2.2  G  4T 1 B

Fig 2-1   Product Model Illustration

MODEL: YTD2.2 G 4T 1B

POWER: 2.2KW    6.5A

INPUT: AC 3PH 380V 50/60HZ

OUTPUT: AC 3PH 0~380V 0~400HZ

NUMBER:

SHANGHAI YATAI INSTRUMENT CO.,LTD

Fig 2-2   Nameplate Illustration

Fig3-1  Inverter Installation Illustration

cabinet

hanging

cuniculus

inverter

C

D          D

inverter

A

B           B

A

Fig3-2  Dimensin Code Illustration

M

PE

U

V

W

L2

L3

L1

～220V

Braking Resistance（Optional）

B

P

Ammeter

IM

GND

Frequency meter

FM

GND

CM

24V

OUT

J

RUN FWD DGT FRQ

F343=1

RUN FWD DGT FRQ

F342=1

F342=1

RUN FWD DGT FRQ

▼

▲

OP6

CM

OP1

OP2

OP3

OP4

OP5

OP7

OP8

GND

I2

V2

Vcc

0～20mA

2.2KΩ

1

2

3

～220V

STOP/RUN

FWD

REV

COM

1234

RS-485

Relay output

12A 125VAC

7A 250VAC

7A 30VDC

TB

TC

TA

Note 1

ControlLoopOutput

ShieldedWire

ControlLoopInput

MainLoopOutput

MainLoopInput

Fig3-3  Standard Wiring Layout for Single-Phase Inverter

M

PE

U

W

Note 2

Braking Unit（Optional）

Frequency meter

P+

B

P

(Ｎ)

Operation Panel

S

T

R

～380V

CM

24V

OUT

J

Press “Mode”for function code.Then press “Set”for previous parameters;press ▲and▼ keys for selecting function code or setting parameters.Press “Set” for input when setting parameter;press ▲and▼ in keypad control mode for dynamic tining.Press “Run”and “Stop/Reset” for start or stop;press”Stop/Reset” for start or stop;press”Stop/Reset”in fault mode to reset inverter.

4 LED showing working status.RUN is on while operating;FWD is on while running forward;REV is on while running reverse;FRQ is on while showing frequency.

Mode

With potentiometer (Vk), for timing in mode of analog signal timing

(see Table 5-1). This potentiometer can not be used together

with external potentiometer.

RUN      FWD       REV       FRQ

Run

▼

RUN FWD DGT FRQ

▼

▲

COM

1234

RS-485

0～20mA

2.2KΩ

1

2

3

～220V

STOP/RUN

FWD

REV

Relay output

12A 125VAC

7A 250VAC

7A 30VDC

TB

TC

TA

Ammeter

IM

GND

LED showing operation frequency, function, parameter values or fault code.

FM

GND

OP6

GND

I2

V2

VCC

CM

OP1

OP2

OP3

OP4

OP5

OP7

OP8

Fig3-4  Standard Wiring Layout for Three-Phase Inverter

ControlLoopOutput

ShieldedWire

ControlLoopInput

MainLoopOutput

MainLoopInput

Set

▲

Mode

External Dimension:①36×70×17mm;   ②66×97×17mm

Fig 4-1 Two Types of Keypad Control Units

Stop

Reset

Min    MAx

Run

▼

▲

Set

Mode

RUN      FWD       REV       FRQ

Stop

Reset

Set

▲

▼

Run

Stop/Reset

Mode

Stop/Reset

▲

▼

Set

Stop/Reset

▲

▼

Set

Mode

Fig 5-1 Forward/reverse Switchover Time

Dead time tr

f

t

Fig 5-2 Jogging Operation

t

f

Removing jogging

operation instruction

Receiving jogging

operation instruction

Jogging Operation

F127

F129

F130

Time(t)

Output Frequency（Hz）

F128

Fig 5-3 Skip Frequency

Fig 5-4 Reverting to manufacturer values

OK!

F 1 0 0

0

Set

F 1 6 0

▲

0

Set

1

▲

YTD-G

Stop/Reset

“FWD” terminal—“open”: stop, “close”: forward running

“REV” terminal—“open”: stop, “close”: reverse running

“CM” terminal—common end

YTD-G

“FWD” terminal—“open”: stop, “close”: running

“REV” terminal—“open”: forward, “close”: reverse

“CM” terminal—common end

YTD-G

“X” terminal—(“open”: stop)

“FWD” terminal—(forward running signal, “close”: forward running)

“REV” terminal—(reverse running signal, “close”: reverse running)

“CM” terminal—common end

YTD-G

“FWD” terminal—(“close”: running)

“X” terminal—(“open”: stop)

“REV” terminal—(forward /reverse running selection) “open”: forward running “close”: reverse running

“CM” terminal—common end

YTD-G

“FWD” terminal—(impulse start/stop signal: forward/stop)

“REV” terminal—(impulse start/stop signal: reverse/stop)

“CM” terminal—common end

Fig 5-5 Auto Circulating Running

Keep running at 3rd speed

After circulating

100 times

3rd

Speed

2nd

Speed

1st

Speed

Start auto

Actual Pulse Input

Count Frequency Division

Fig 5-6 Set Count times & Fixed Count Times

Fig 5-7 Torque Promotion

V（％）

Turnover Frequency

1

15

f

Fig5-8 Polygonal-Line Type V/F

f

V（％）

F118

F505　F507

F508

F506

F502

F509

F515

Hz

ｔ

F518

F516

F517

I(%)

ｔ

Fig 5-9 DC Braking

Fig 5-10 PI Adjusting

变频器适配电机功率

实际电机功率

F808

F807

Corresponding

frequency

Input Analog

F800

F801

F808

F807

F800

F801

Corresponding

frequency

Input Analog

Fig 5-12 Proportion Mode of Analog Adjusting

Fig 6-4 Auto-Circulating Operation (different operation direction between segment speeds)

F321

F319

F317

F316

F315

F313

F310

F311

F309

F305

F307

F303

F304

F301

Time

Frequency

Fig 6-3 Auto-Circulating Operation (stop/wait time>0)

4thspeed

F320

3rdspeed

F314

2ndspeed

F308

1stspeed

F302

F321

F319

F317

F316

F315

F313

F310

F311

F309

F305

F307

F303

F304

F301

Time

Frequency

Fig 6-2 Auto-Circulating Operation (stop/wait time=0)

Frequency

时间

F304

F333

F310

F303

F309

F315

F316

F322

F328

F321

F327

F340

F334

F339

F333

F337

F331

F325

F327

F321

F315

F319

F313

F307

F309

F301

F303

1stspeed

F302

2ndspeed

F308

3rdspeed

F314

4thspeed

F320

5thspeed

F326

6thspeed

F332

7thspeed

F338

6thspeed

F332

5thspeed

F326

4thspeed

F320

3rdspeed

F314

2ndspeed

F308

1stspeed

F302

4thspeed

F320

3rdspeed

F314

2ndspeed

F308

1stspeed

F302

F120

F120